## Section 3 Results
Results obtained by computer simulation of the case study using COMSOL ( Electromagnetic Field Modeling ) and ATP ( Lumped Parameter Modeling )
INPUT PARAMETERS | [14 empty] | COMPUTACIONAL SIMULATION RESULTS
Project data | [7 empty] | Lumped parameter modeling according Section 3 | [6 empty] | Electromagnetic Field Modeling using COMSOL |  |  |  |  | Lumped parameter modeling using ATP
L (m) | h (m) | p (Ω.m) | Cg (m) | pcu(Ω/mm².km) | A (mm²) | Rs (Ω/km) | Zs (Ω/km) | Zs_lumped (Ω) | Rp_lumped (Ω) | Rs_lumped (Ω) | Lp_lumped (H) | Rf (Ω) | k | Rc (Ω) | Lumped port impedance (Ω) | R (Ω) | X (Ω) | ¦Zmed¦ (Ω) | θ (°) | ¦Zmed¦(Ω) [23] | Erro (%) [23] | ¦Zmed¦(Ω) [Proposed] | Erro (%) [Proposed]
300 | 1 | 100 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,75613335208976i | 0,0690868268663922+0,226840005626928i | 0.88093 | 0.069087 | 2.2966e-05 | 1.2168 | 0.7 | 4.8947 | 1,3439069021425247+0,5298764706375344i | 1.3439 | 0.52988 | 1.4446 | 21.5184 | 1.7433 | 20.68% | 1.2893 | -10.75%
300 | 1 | 300 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,790629777953939i | 0,0690868268663922+0,237188933386182i | 2.6428 | 0.069087 | 2.4014e-05 | 3.6504 | 0.7 | 14.6841 | 3,582376770583496+0,7067946590924175i | 3.5824 | 0.70679 | 3.6514 | 11.161 | 4.7934 | 31.27% | 3.4972 | -4.224%
300 | 1 | 5252 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,880514845242007i | 0,0690868268663922+0,264154453572602i | 46.2663 | 0.069087 | 2.6744e-05 | 63.907 | 0.7 | 257.071 | 59,91921539522289+0,7443470526300021i | 59.9192 | 0.74435 | 59.9238 | 0.71172 | 80.5331 | 34.39% | 59.456 | -0.7807%
300 | 1 | 10240 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,90148039486557i | 0,0690868268663922+0,270444118459671i | 90.2069 | 0.069087 | 2.7381e-05 | 124.6 | 0.7 | 501.2162 | 116,79795067665087+0,6319137801647258i | 116.798 | 0.63191 | 116.7997 | 0.30999 | 154.3222 | 32.13% | 115.91 | -0.7617%
300 | 1 | 2100 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,851731356634276i | 0,0690868268663922+0,255519406990283i | 18.4995 | 0.069087 | 2.587e-05 | 4.1899 | 0.7 | 52.9419 | 6,04335854491927+2,965067414146472i | 6.0434 | 2.9651 | 6.7316 | 26.1341 | 8.8542 | 31.53% | 5.989 | -11.03%
Where:
L is the length of the horizontal electrode (m)
h is the depth of burial (m)
ρ is the medium earth resistivity (Ω.m)
Cg is the geometric mean radius of the electrode (m)
pcu is the resistivity of copper (Ω/mm².km)
A is the cross-sectional area of the horizontal eletrode (mm2)
Zs is the horizontal electrodes self-impedance (Ω)
Rp is the horizontal electrodes grounding resistance (Ω)
Rf corresponds to the turbine grounding resistance (Ω)
Rs is the series resistance of the horizontal electrode (Ω/km)
Rc is the resistance parallel to the measurement loop to represent the mutual resistance between the turbine grounding under test and its adjacent horizontal electrode
k is the adjustment parameter introduced to tuning the model

## Section 4 Results
Parameter k survey
Results obtained by computer simulation of the case study in COMSOL
L (m) | ρ (m) | Rmed_wire_10L (Ω) | Rmed_wire_11.4m (Ω) | Rf (Ω) | Rp (Ω) | 2.Rp (Ω) | Semisphere_rp(Ω) | Rmed_lumped_10L (Ω) | Rmed_lumped_11.4m (Ω) | AE | k
80 | 5252 | 128.5664 | 91.6683 | 62.7068 | 65.8596 | 131.7193 | 6.3459 | 131.78 | 94.667 | -0.26367 | 0.73633
90 | 5252 | 122.9787 | 87.0173 | 62.7068 | 60.2719 | 120.5439 | 6.9343 | 125.9 | 89.865 | -0.26926 | 0.73074
100 | 5252 | 114.8196 | 83.7113 | 62.7068 | 52.1128 | 104.2255 | 8.0199 | 117.42 | 82.653 | -0.28015 | 0.71985
150 | 5252 | 97.2516 | 72.4684 | 62.7068 | 34.5447 | 69.0895 | 12.0985 | 98.999 | 68.005 | -0.30073 | 0.69927
200 | 5252 | 89.4691 | 68.7868 | 62.7068 | 26.7623 | 53.5246 | 15.6168 | 90.751 | 63.1 | -0.29473 | 0.70527
250 | 5252 | 83.3147 | 65.4931 | 62.7068 | 20.6079 | 41.2157 | 20.2806 | 84.341 | 60.195 | -0.2775 | 0.7225
300 | 5252 | 80.6177 | 63.8902 | 62.7068 | 17.9109 | 35.8219 | 23.3344 | 80.778 | 56.61 | -0.2978 | 0.7022
350 | 5252 | 78.6422 | 61.2476 | 62.7068 | 15.9354 | 31.8708 | 26.2272 | 79.361 | 54.192 | -0.3109 | 0.6891
400 | 5252 | 76.1279 | 60.0108 | 62.7068 | 13.4211 | 26.8421 | 31.1407 | 76.751 | 52.559 | -0.3096 | 0.6904
500 | 5252 | 73.4093 | 58.9608 | 62.7068 | 10.7025 | 21.405 | 39.0508 | 73.888 | 50.89 | -0.30676 | 0.69324
600 | 5252 | 72.3253 | 59.0534 | 62.7068 | 9.6184 | 19.2369 | 43.452 | 72.701 | 50.76 | -0.29817 | 0.70183
800 | 5252 | 69.2223 | 57.0188 | 62.7068 | 6.5155 | 13.031 | 64.1457 | 69.643 | 48.729 | -0.29605 | 0.70395
Where:
L is the length of the horizontal electrode (m).
ρ is the medium earth resistivity (Ω.m).
Rmed_wire_10L is the clamp-on reading taken with a distance of 10L between the turbine grounding and the horizontal electrode wire (Ω).
Rmed_wire_11.4m is the clamp-on reading taken with a distance of 11.4 m between the turbine grounding and the horizontal electrode wire (Ω).
Rf is the grounding resistance of the turbine grounding (Ω).
Rp is the grounding resistance of the horizontal electrode (Ω).
Semisphere_rp is the radius of the two semi-spherical electrodes that represent a horizontal electrode according to the lumped parameter modeling (m) .
Rmed_lumped_10L is the clamp-on reading taken with a distance of 10L between the turbine grounding and the horizontal electrode represented by semi-spheres (Ω) .
Rmed_lumped_11.4m is the clamp-on reading taken with a distance of 11.4 m between the turbine grounding and the horizontal electrode represented by semi-spheres (Ω) .
AE is the expected absolute error caused by mutual coupling between nearby electrodes and modeling of the horizontal electrode through lumped parameter (%).
k is the adjustment parameter introduced to tuning the model