## Section 3 Results
Results obtained by computer simulation of the case study using COMSOL ( Electromagnetic Field Modeling ) and ATP ( Lumped Parameter Modeling )
INPUT PARAMETERS | [14 empty] | COMPUTACIONAL SIMULATION RESULTS
Project data | [7 empty] | Lumped parameter modeling according Section 3 | [6 empty] | Electromagnetic Field Modeling using COMSOL |  |  |  |  | Lumped parameter modeling using ATP
L (m) | h (m) | p (Ω.m) | Cg (m) | pcu(Ω/mm².km) | A (mm²) | Rs (Ω/km) | Zs (Ω/km) | Zs_lumped (Ω) | Rp_lumped (Ω) | Rs_lumped (Ω) | Lp_lumped (H) | Rf (Ω) | k | Rc (Ω) | Lumped port impedance (Ω) | R (Ω) | X (Ω) | ¦Zmed¦ (Ω) | θ (°) | ¦Zmed¦(Ω) [23] | Erro (%) [23] | ¦Zmed¦(Ω) [Proposed] | Erro (%) [Proposed]
300 | 1 | 100 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,75613335208976i | 0,0690868268663922+0,226840005626928i | 0.88093 | 0.069087 | 2.2966e-05 | 1.2168 | 0.7 | 4.8947 | 1,3439069021425247+0,5298764706375344i | 1.3439 | 0.52988 | 1.4446 | 21.5184 | 1.7433 | 20.68% | 1.2893 | -10.75%
300 | 1 | 300 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,790629777953939i | 0,0690868268663922+0,237188933386182i | 2.6428 | 0.069087 | 2.4014e-05 | 3.6504 | 0.7 | 14.6841 | 3,582376770583496+0,7067946590924175i | 3.5824 | 0.70679 | 3.6514 | 11.161 | 4.7934 | 31.27% | 3.4972 | -4.224%
300 | 1 | 5252 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,880514845242007i | 0,0690868268663922+0,264154453572602i | 46.2663 | 0.069087 | 2.6744e-05 | 63.907 | 0.7 | 257.071 | 59,91921539522289+0,7443470526300021i | 59.9192 | 0.74435 | 59.9238 | 0.71172 | 80.5331 | 34.39% | 59.456 | -0.7807%
300 | 1 | 10240 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,90148039486557i | 0,0690868268663922+0,270444118459671i | 90.2069 | 0.069087 | 2.7381e-05 | 124.6 | 0.7 | 501.2162 | 116,79795067665087+0,6319137801647258i | 116.798 | 0.63191 | 116.7997 | 0.30999 | 154.3222 | 32.13% | 115.91 | -0.7617%
300 | 1 | 2100 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,851731356634276i | 0,0690868268663922+0,255519406990283i | 18.4995 | 0.069087 | 2.587e-05 | 4.1899 | 0.7 | 52.9419 | 6,04335854491927+2,965067414146472i | 6.0434 | 2.9651 | 6.7316 | 26.1341 | 8.8542 | 31.53% | 5.989 | -11.03%
Where:
L is the length of the horizontal electrode (m)
h is the depth of burial (m)
ρ is the medium earth resistivity (Ω.m)
Cg is the geometric mean radius of the electrode (m)
pcu is the resistivity of copper (Ω/mm².km)
A is the cross-sectional area of the horizontal eletrode (mm2)
Zs is the horizontal electrodes self-impedance (Ω)
Rp is the horizontal electrodes grounding resistance (Ω)
Rf corresponds to the turbine grounding resistance (Ω)
Rs is the series resistance of the horizontal electrode (Ω/km)
Rc is the resistance parallel to the measurement loop to represent the mutual resistance between the turbine grounding under test and its adjacent horizontal electrode
k is the adjustment parameter introduced to tuning the model

## Section 4 Results
Parameter k survey
Results obtained by computer simulation of the case study in COMSOL
lenght (m) | ρ (m) | freq (Hz) | Lumped port impedance 10xlenght (Ω) | Rmed∞ (Ω) | Xmed∞ (Ω) | Zmed∞ (Ω) | θmed∞ (Ω) | Lumped port impedance 11,4m (Ω) | Rmed11 (Ω) | Xmed11 (Ω) | Zmed11 (Ω) | θmed11 (°) | Lumped port impedance mutual | Rm (Ω) | Xm (Ω) | Zm (Ω) | θm (°) | Rf (Ω) [23] | Rp (Ω) [23] | Erro_CGM (%) | 2Rp (Ω) [23] | 2Rp_radius (Ω) [23]
10 | 20 | 0 | 1,2878659088567024-2,3133201273767093E-13i | 1.2879 | -2.3133e-13 | 1.2879 | -1.0292e-11 | 1,0446566653723106-1,7715404249410847E-13i | 1.0447 | -1.7715e-13 | 1.0447 | -9.7163e-12 | 0,24320924348439-5,4177970243562E-14i | 0.24321 | -5.4178e-14 | 0.24321 | -1.2763e-11 | 0.23879 | 1.0491 | 337.5% | 2.0981 | 1.5171
20 | 20 | 0 | 0,9377689779314281-1,7527011735794723E-13i | 0.93777 | -1.7527e-13 | 0.93777 | -1.0709e-11 | 0,7075435253159804-1,2298502730194857E-13i | 0.70754 | -1.2299e-13 | 0.70754 | -9.9591e-12 | 0,230225452615448-5,2285090055999E-14i | 0.23023 | -5.2285e-14 | 0.23023 | -1.3012e-11 | 0.23879 | 0.69898 | 196.3% | 1.398 | 2.277
30 | 20 | 0 | 0,7785814617096696-1,482737224117265E-13i | 0.77858 | -1.4827e-13 | 0.77858 | -1.0911e-11 | 0,5611309728426628-9,878698712852656E-14i | 0.56113 | -9.8787e-14 | 0.56113 | -1.0087e-11 | 0,217450488867007-4,94867352831995E-14i | 0.21745 | -4.9487e-14 | 0.21745 | -1.3039e-11 | 0.23879 | 0.53979 | 135% | 1.0796 | 2.9485
40 | 20 | 0 | 0,6729692137062832-1,306403749819951E-13i | 0.67297 | -1.3064e-13 | 0.67297 | -1.1123e-11 | 0,47946477838885365-8,53149402216309E-14i | 0.47946 | -8.5315e-14 | 0.47946 | -1.0195e-11 | 0,19350443531743-4,53254347603641E-14i | 0.1935 | -4.5325e-14 | 0.1935 | -1.3421e-11 | 0.23879 | 0.43418 | 100.8% | 0.86835 | 3.6657
50 | 20 | 0 | 0,6085243460548915-1,1869549315646745E-13i | 0.60852 | -1.187e-13 | 0.60852 | -1.1176e-11 | 0,4280202323736097-7,639041422700109E-14i | 0.42802 | -7.639e-14 | 0.42802 | -1.0226e-11 | 0,180504113681282-4,2305078929466E-14i | 0.1805 | -4.2305e-14 | 0.1805 | -1.3429e-11 | 0.23879 | 0.36973 | 79.24% | 0.73946 | 4.3046
60 | 20 | 0 | 0,5596921897430254-1,0918343272180885E-13i | 0.55969 | -1.0918e-13 | 0.55969 | -1.1177e-11 | 0,3933980954346844-7,081858365073939E-14i | 0.3934 | -7.0819e-14 | 0.3934 | -1.0314e-11 | 0,166294094308341-3,83648490710687E-14i | 0.16629 | -3.8365e-14 | 0.16629 | -1.3218e-11 | 0.23879 | 0.3209 | 64.75% | 0.6418 | 4.9596
70 | 20 | 0 | 0,5073990262061271-9,908412629299576E-14i | 0.5074 | -9.9084e-14 | 0.5074 | -1.1189e-11 | 0,3705438777414371-6,671516044480415E-14i | 0.37054 | -6.6715e-14 | 0.37054 | -1.0316e-11 | 0,13685514846469-3,23689658481916E-14i | 0.13686 | -3.2369e-14 | 0.13686 | -1.3552e-11 | 0.23879 | 0.26861 | 55.17% | 0.53721 | 5.9252
80 | 20 | 0 | 0,48958822222868187-9,557097857141679E-14i | 0.48959 | -9.5571e-14 | 0.48959 | -1.1185e-11 | 0,34907981099020763-6,296474799002369E-14i | 0.34908 | -6.2965e-14 | 0.34908 | -1.0335e-11 | 0,140508411238474-3,26062305813931E-14i | 0.14051 | -3.2606e-14 | 0.14051 | -1.3296e-11 | 0.23879 | 0.2508 | 46.19% | 0.50159 | 6.346
90 | 20 | 0 | 0,46831175077630155-9,121185246434701E-14i | 0.46831 | -9.1212e-14 | 0.46831 | -1.1159e-11 | 0,33136833767790763-5,97210118374121E-14i | 0.33137 | -5.9721e-14 | 0.33137 | -1.0326e-11 | 0,136943413098394-3,14908406269349E-14i | 0.13694 | -3.1491e-14 | 0.13694 | -1.3175e-11 | 0.23879 | 0.22952 | 38.77% | 0.45904 | 6.9343
100 | 20 | 0 | 0,4372402966145142-6,801372108491488E-8i | 0.43724 | -6.8014e-08 | 0.43724 | -8.9125e-06 | 0,31877972180478537-5,799302922374932E-14i | 0.31878 | -5.7993e-14 | 0.31878 | -1.0423e-11 | 0,118460574809729-6,80136630918856E-08i | 0.11846 | -6.8014e-08 | 0.11846 | -3.2896e-05 | 0.23879 | 0.19845 | 33.5% | 0.3969 | 8.02
150 | 20 | 0 | 0,37034072908576254-7,237263277728597E-14i | 0.37034 | -7.2373e-14 | 0.37034 | -1.1197e-11 | 0,27596409949224543+1,8480439566205039E-6i | 0.27596 | 1.848e-06 | 0.27596 | 0.00038369 | 0,094376629593517-1,84804402899313E-06i | 0.094377 | -1.848e-06 | 0.094377 | -0.0011219 | 0.23879 | 0.13155 | 15.57% | 0.2631 | 12.0986
200 | 20 | 0 | 0,3407042301789263+2,1458208174026564E-13i | 0.3407 | 2.1458e-13 | 0.3407 | 3.6086e-11 | 0,261946091464479-4,741184176242074E-14i | 0.26195 | -4.7412e-14 | 0.26195 | -1.037e-11 | 0,078758138714447+2,61993923502686E-13i | 0.078758 | 2.6199e-13 | 0.078758 | 1.906e-10 | 0.23879 | 0.10191 | 9.696% | 0.20382 | 15.6169
250 | 20 | 0 | 0,3172684557107425-1,9269608884751506E-7i | 0.31727 | -1.927e-07 | 0.31727 | -3.4799e-05 | 0,24940297004353776-4,500666983990893E-14i | 0.2494 | -4.5007e-14 | 0.2494 | -1.0339e-11 | 0,067865485667205-1,92696043840845E-07i | 0.067865 | -1.927e-07 | 0.067865 | -0.00016268 | 0.23879 | 0.078476 | 4.444% | 0.15695 | 20.2806
300 | 20 | 0 | 0,306998019286339-1,0923562094045121E-14i | 0.307 | -1.0924e-14 | 0.307 | -2.0387e-12 | 0,2432997338432089-4,3720007221080623E-14i | 0.2433 | -4.372e-14 | 0.2433 | -1.0296e-11 | 0,063698285443131+3,27964451270355E-14i | 0.063698 | 3.2796e-14 | 0.063698 | 2.95e-11 | 0.23879 | 0.068206 | 1.888% | 0.13641 | 23.3345
350 | 20 | 0 | 0,29947523599224074-5,772440847766374E-14i | 0.29948 | -5.7724e-14 | 0.29948 | -1.1044e-11 | 0,23323564024079785-1,1270894127695334E-7i | 0.23324 | -1.1271e-07 | 0.23324 | -2.7688e-05 | 0,066239595751443+1,12708883552545E-07i | 0.06624 | 1.1271e-07 | 0.06624 | 9.7491e-05 | 0.23879 | 0.060683 | -2.327% | 0.12137 | 26.2272
400 | 20 | 0 | 0,2899003257565196-3,3326153342184584E-8i | 0.2899 | -3.3326e-08 | 0.2899 | -6.5866e-06 | 0,22852614963268367+1,2425055892750937E-13i | 0.22853 | 1.2425e-13 | 0.22853 | 3.1152e-11 | 0,061374176123836-3,33262775927434E-08i | 0.061374 | -3.3326e-08 | 0.061374 | -3.1112e-05 | 0.23879 | 0.051108 | -4.299% | 0.10222 | 31.1408
500 | 20 | 0 | 0,2795481447448776-5,074949894906852E-13i | 0.27955 | -5.0749e-13 | 0.27955 | -1.0402e-10 | 0,2245268511106448+3,8878230861860264E-7i | 0.22453 | 3.8878e-07 | 0.22453 | 9.9211e-05 | 0,055021293634233-3,88782816113591E-07i | 0.055021 | -3.8878e-07 | 0.055021 | -0.00040485 | 0.23879 | 0.040756 | -5.974% | 0.081512 | 39.0506
600 | 20 | 0 | 0,2754209055001616-5,245069878865292E-14i | 0.27542 | -5.2451e-14 | 0.27542 | -1.0911e-11 | 0,2248799370708311+1,528260256344397E-7i | 0.22488 | 1.5283e-07 | 0.22488 | 3.8938e-05 | 0,05054096842933-1,52826078085138E-07i | 0.050541 | -1.5283e-07 | 0.050541 | -0.00017325 | 0.23879 | 0.036629 | -5.826% | 0.073258 | 43.4508
800 | 20 | 0 | 0,2636044701341971-1,6553574456896276E-7i | 0.2636 | -1.6554e-07 | 0.2636 | -3.598e-05 | 0,21713223336734014-3,8801735844656765E-14i | 0.21713 | -3.8802e-14 | 0.21713 | -1.0239e-11 | 0,046472236766857-1,65535705767226E-07i | 0.046472 | -1.6554e-07 | 0.046472 | -0.00020409 | 0.23879 | 0.024812 | -9.071% | 0.049625 | 64.1434
1000 | 20 | 0 | 0,2583445182629951-4,585961040304634E-14i | 0.25834 | -4.586e-14 | 0.25834 | -1.0171e-11 | 0,2166749181732941-3,865690790008461E-14i | 0.21667 | -3.8657e-14 | 0.21667 | -1.0222e-11 | 0,041669600089701-7,2027025029617E-15i | 0.04167 | -7.2027e-15 | 0.04167 | -9.9037e-12 | 0.23879 | 0.019552 | -9.262% | 0.039105 | 81.3992
1500 | 20 | 0 | 0,2571822865393841+2,8341942618078962E-14i | 0.25718 | 2.8342e-14 | 0.25718 | 6.3141e-12 | 0,21472977783477196-3,678618451253194E-14i | 0.21473 | -3.6786e-14 | 0.21473 | -9.8156e-12 | 0,042452508704613+6,51281271306108E-14i | 0.042453 | 6.5128e-14 | 0.042453 | 8.79e-11 | 0.23879 | 0.01839 | -10.08% | 0.03678 | 86.5435 | θ
10 | 20 | 1572 | 1,3824735885066017+0,8921377284316998i | 1.3825 | 0.89214 | 1.6453 | 32.835 | 1,055252346401894+0,0826337198797666i | 1.0553 | 0.082634 | 1.0585 | 4.4775 | 0,32722124210471+0,809504008551932i | 0.32722 | 0.8095 | 0.87314 | 67.9902 | 0.23879 | 1.0491 | 343.3% | 2.0981 | 1.5171
20 | 20 | 1572 | 1,1815652747303855+1,8592136743727858i | 1.1816 | 1.8592 | 2.2029 | 57.5633 | 0,715483906573916+0,10351080867194817i | 0.71548 | 0.10351 | 0.72293 | 8.232 | 0,466081368156464+1,75570286570083i | 0.46608 | 1.7557 | 1.8165 | 75.1328 | 0.23879 | 0.69898 | 202.7% | 1.398 | 2.277
30 | 20 | 1572 | 1,182088609338406+2,8168355755979i | 1.1821 | 2.8168 | 3.0548 | 67.2346 | 0,5726556783186979+0,12503832625459135i | 0.57266 | 0.12504 | 0.58615 | 12.3171 | 0,609432931019703+2,69179724934331i | 0.60943 | 2.6918 | 2.7599 | 77.2431 | 0.23879 | 0.53979 | 145.5% | 1.0796 | 2.9485
40 | 20 | 1572 | 1,2401043506480003+3,7386503470025687i | 1.2401 | 3.7387 | 3.939 | 71.6494 | 0,49749436290232996+0,14551401186137305i | 0.49749 | 0.14551 | 0.51834 | 16.3039 | 0,742609987745671+3,59313633514119i | 0.74261 | 3.5931 | 3.6691 | 78.3228 | 0.23879 | 0.43418 | 117.1% | 0.86835 | 3.6657
50 | 20 | 1572 | 1,343458408155137+4,652996256467771i | 1.3435 | 4.653 | 4.8431 | 73.895 | 0,45324310871684964+0,16609686210069538i | 0.45324 | 0.1661 | 0.48272 | 20.126 | 0,890215299438281+4,48689939436707i | 0.89022 | 4.4869 | 4.5744 | 78.7781 | 0.23879 | 0.36973 | 102.2% | 0.73946 | 4.3046
60 | 20 | 1572 | 1,4648348605184756+5,609632621512879i | 1.4648 | 5.6096 | 5.7977 | 75.3652 | 0,42640139623477985+0,1838764099485653i | 0.4264 | 0.18388 | 0.46436 | 23.3271 | 1,03843346428369+5,42575621156431i | 1.0384 | 5.4258 | 5.5242 | 79.1652 | 0.23879 | 0.3209 | 94.46% | 0.6418 | 4.9596
70 | 20 | 1572 | 1,583287976917925+6,492663278927205i | 1.5833 | 6.4927 | 6.6829 | 76.2954 | 0,4122485297936554+0,19917104065096686i | 0.41225 | 0.19917 | 0.45784 | 25.7867 | 1,17103944712427+6,29349223827623i | 1.171 | 6.2935 | 6.4015 | 79.4594 | 0.23879 | 0.26861 | 91.73% | 0.53721 | 5.9252
80 | 20 | 1572 | 1,7396233322937176+7,257304200540257i | 1.7396 | 7.2573 | 7.4629 | 76.5202 | 0,4003461413151777+0,21376608433142344i | 0.40035 | 0.21377 | 0.45384 | 28.1001 | 1,33927719097853+7,04353811620883i | 1.3393 | 7.0435 | 7.1697 | 79.2341 | 0.23879 | 0.2508 | 90.06% | 0.50159 | 6.346
90 | 20 | 1572 | 1,9024502344126755+8,317645943363674i | 1.9025 | 8.3176 | 8.5324 | 77.1167 | 0,39845602180694856+0,2240511720908356i | 0.39846 | 0.22405 | 0.45713 | 29.349 | 1,50399421260572+8,09359477127284i | 1.504 | 8.0936 | 8.2321 | 79.4731 | 0.23879 | 0.22952 | 91.43% | 0.45904 | 6.9343
100 | 20 | 1572 | 2,0397569439890075+8,860327749965114i | 2.0398 | 8.8603 | 9.0921 | 77.0357 | 0,3933562697829926+0,23115364935093763i | 0.39336 | 0.23115 | 0.45625 | 30.4404 | 1,64640067420601+8,62917410061417i | 1.6464 | 8.6292 | 8.7848 | 79.1981 | 0.23879 | 0.19845 | 91.06% | 0.3969 | 8.02
150 | 20 | 1572 | 2,8060957916315448+12,574561584302785i | 2.8061 | 12.5746 | 12.8839 | 77.4202 | 0,40437294493800896+0,2484743772474574i | 0.40437 | 0.24847 | 0.47461 | 31.5694 | 2,40172284669353+12,3260872070552i | 2.4017 | 12.3261 | 12.5579 | 78.9741 | 0.23879 | 0.13155 | 98.76% | 0.2631 | 12.0986
200 | 20 | 1572 | 3,585520186922237+16,299814683498777i | 3.5855 | 16.2998 | 16.6895 | 77.5941 | 0,4076429373844291+0,24901643094005377i | 0.40764 | 0.24902 | 0.47768 | 31.4195 | 3,1778772495378+16,0507982525586i | 3.1779 | 16.0508 | 16.3624 | 78.8009 | 0.23879 | 0.10191 | 100% | 0.20382 | 15.6169
250 | 20 | 1572 | 4,371586921599124+20,533919290683937i | 4.3716 | 20.5339 | 20.9941 | 77.9814 | 0,4072537293401423+0,24981461706594607i | 0.40725 | 0.24981 | 0.47777 | 31.5255 | 3,96433319225898+20,284104673618i | 3.9643 | 20.2841 | 20.6679 | 78.9415 | 0.23879 | 0.078476 | 100.1% | 0.15695 | 20.2806
300 | 20 | 1572 | 5,155471489700972+23,775863073927532i | 5.1555 | 23.7759 | 24.3284 | 77.7656 | 0,40659648120734265+0,2473015984580495i | 0.4066 | 0.2473 | 0.4759 | 31.309 | 4,74887500849363+23,5285614754695i | 4.7489 | 23.5286 | 24.003 | 78.589 | 0.23879 | 0.068206 | 99.29% | 0.13641 | 23.3345
350 | 20 | 1572 | 5,871757628349783+24,679360232263342i | 5.8718 | 24.6794 | 25.3683 | 76.6169 | 0,4088799259225428+0,24804266930193478i | 0.40888 | 0.24804 | 0.47823 | 31.2426 | 5,46287770242724+24,4313175629614i | 5.4629 | 24.4313 | 25.0346 | 77.3959 | 0.23879 | 0.060683 | 100.3% | 0.12137 | 26.2272
400 | 20 | 1572 | 6,612552653936263+27,735956770004822i | 6.6126 | 27.736 | 28.5133 | 76.5904 | 0,4077792666568708+0,25016450491919656i | 0.40778 | 0.25016 | 0.4784 | 31.5283 | 6,20477338727939+27,4857922650856i | 6.2048 | 27.4858 | 28.1774 | 77.279 | 0.23879 | 0.051108 | 100.3% | 0.10222 | 31.1408
500 | 20 | 1572 | 8,021994617940083+32,326824854397444i | 8.022 | 32.3268 | 33.3073 | 76.0634 | 0,40724789409788864+0,2483523580903954i | 0.40725 | 0.24835 | 0.477 | 31.3761 | 7,61474672384219+32,078472496307i | 7.6147 | 32.0785 | 32.9699 | 76.6464 | 0.23879 | 0.040756 | 99.76% | 0.081512 | 39.0506
600 | 20 | 1572 | 9,484562371325755+38,834086783045315i | 9.4846 | 38.8341 | 39.9755 | 76.2752 | 0,4084336355046492+0,25121472825654423i | 0.40843 | 0.25121 | 0.47951 | 31.5944 | 9,0761287358211+38,5828720547888i | 9.0761 | 38.5829 | 39.636 | 76.7626 | 0.23879 | 0.036629 | 100.8% | 0.073258 | 43.4508
800 | 20 | 1572 | 11,911584731349102+44,22589614781163i | 11.9116 | 44.2259 | 45.8019 | 74.9259 | 0,405377418735982+0,24795526591370268i | 0.40538 | 0.24796 | 0.4752 | 31.4527 | 11,5062073126131+43,9779408818979i | 11.5062 | 43.9779 | 45.4582 | 75.338 | 0.23879 | 0.024812 | 99% | 0.049625 | 64.1434
1000 | 20 | 1572 | 14,278299653066838+52,12610106289981i | 14.2783 | 52.1261 | 54.0463 | 74.6814 | 0,4086396533337049+0,24785382435472803i | 0.40864 | 0.24785 | 0.47793 | 31.2382 | 13,8696599997331+51,8782472385451i | 13.8697 | 51.8782 | 53.7003 | 75.032 | 0.23879 | 0.019552 | 100.1% | 0.039105 | 81.3992
1500 | 20 | 1572 | 18,616+71,05i | 18.616 | 71.05 | 73.4483 | 75.3178 | 0,40982+0,24786i | 0.40982 | 0.24786 | 0.47894 | 31.1656 | 18,20618+70,80214i | 18.2062 | 70.8021 | 73.1055 | 75.5793 | 0.23879 | 0.01839 | 100.6% | 0.03678 | 86.5435
10 | 100 | 0 | 6,439329592601053-5,783300439733992E-12i | 6.4393 | -5.7833e-12 | 6.4393 | -5.1459e-11 | 5,2232832693203815-4,428850948286552E-12i | 5.2233 | -4.4289e-12 | 5.2233 | -4.8581e-11 | 1,21604632328067-1,35444949144744E-12i | 1.216 | -1.3544e-12 | 1.216 | -6.3817e-11 | 1.194 | 5.2454 | 337.5% | 10.4907 | 1.5171
20 | 100 | 0 | 4,6888449930957155-4,381753659487498E-12i | 4.6888 | -4.3818e-12 | 4.6888 | -5.3543e-11 | 3,5377176221356907-3,0746256968408217E-12i | 3.5377 | -3.0746e-12 | 3.5377 | -4.9796e-11 | 1,15112737096002-1,30712796264667E-12i | 1.1511 | -1.3071e-12 | 1.1511 | -6.506e-11 | 1.194 | 3.4949 | 196.3% | 6.9898 | 2.277
30 | 100 | 0 | 3,892905087970625-3,706881421497692E-12i | 3.8929 | -3.7069e-12 | 3.8929 | -5.4558e-11 | 2,8056548933979832-2,469674712778461E-12i | 2.8057 | -2.4697e-12 | 2.8057 | -5.0435e-11 | 1,08725019457264-1,23720670871923E-12i | 1.0873 | -1.2372e-12 | 1.0873 | -6.5198e-11 | 1.194 | 2.6989 | 135% | 5.3979 | 2.9485
40 | 100 | 0 | 3,364851921581513-3,2660771013138432E-12i | 3.3649 | -3.2661e-12 | 3.3649 | -5.5614e-11 | 2,397325288081893-2,132865681320732E-12i | 2.3973 | -2.1329e-12 | 2.3973 | -5.0975e-11 | 0,96752663349962-1,13321141999311E-12i | 0.96753 | -1.1332e-12 | 0.96753 | -6.7107e-11 | 1.194 | 2.1709 | 100.8% | 4.3418 | 3.6657
50 | 100 | 0 | 3,0426182438043745-6,8508442552567E-12i | 3.0426 | -6.8508e-12 | 3.0426 | -1.2901e-10 | 2,1401013150986725-1,9097600285380665E-12i | 2.1401 | -1.9098e-12 | 2.1401 | -5.1129e-11 | 0,9025169287057-4,94108422671864E-12i | 0.90252 | -4.9411e-12 | 0.90252 | -3.1368e-10 | 1.194 | 1.8487 | 79.24% | 3.6973 | 4.3046
60 | 100 | 0 | 2,7984593282316217-2,7296077715571976E-12i | 2.7985 | -2.7296e-12 | 2.7985 | -5.5886e-11 | 1,966990656382849-1,771491403174855E-12i | 1.967 | -1.7715e-12 | 1.967 | -5.1601e-11 | 0,83146867184878-9,5811636838234E-13i | 0.83147 | -9.5812e-13 | 0.83147 | -6.6023e-11 | 1.194 | 1.6045 | 64.75% | 3.209 | 4.9596
70 | 100 | 0 | 2,5369936739885657-2,479907612119096E-12i | 2.537 | -2.4799e-12 | 2.537 | -5.6007e-11 | 1,852720304066333-1,6673055626625565E-12i | 1.8527 | -1.6673e-12 | 1.8527 | -5.1562e-11 | 0,68427336992223-8,1260204945654E-13i | 0.68427 | -8.126e-13 | 0.68427 | -6.8041e-11 | 1.194 | 1.343 | 55.17% | 2.6861 | 5.9252
80 | 100 | 0 | 2,4479420004521057-2,3990206748976202E-12i | 2.4479 | -2.399e-12 | 2.4479 | -5.6151e-11 | 1,745405580479139-1,574121593735903E-12i | 1.7454 | -1.5741e-12 | 1.7454 | -5.1673e-11 | 0,70253641997297-8,2489908116172E-13i | 0.70254 | -8.249e-13 | 0.70254 | -6.7275e-11 | 1.194 | 1.254 | 46.19% | 2.508 | 6.346
90 | 100 | 0 | 2,3415542695769225-2,2802169547674365E-12i | 2.3416 | -2.2802e-12 | 2.3416 | -5.5795e-11 | 1,6568401056873507-1,4930266339690956E-12i | 1.6568 | -1.493e-12 | 1.6568 | -5.1631e-11 | 0,68471416388957-7,8719032079834E-13i | 0.68471 | -7.8719e-13 | 0.68471 | -6.5871e-11 | 1.194 | 1.1476 | 38.77% | 2.2952 | 6.9343
100 | 100 | 0 | 2,1861983438671824-2,1443707059435707E-12i | 2.1862 | -2.1444e-12 | 2.1862 | -5.62e-11 | 1,593896334512082-1,4447097383509066E-12i | 1.5939 | -1.4447e-12 | 1.5939 | -5.1933e-11 | 0,5923020093551-6,9966096759267E-13i | 0.5923 | -6.9966e-13 | 0.5923 | -6.7681e-11 | 1.194 | 0.99224 | 33.5% | 1.9845 | 8.02
150 | 100 | 0 | 1,851700337469165-1,5765995683508556E-12i | 1.8517 | -1.5766e-12 | 1.8517 | -4.8784e-11 | 1,3798248258790984+3,714067854396251E-8i | 1.3798 | 3.7141e-08 | 1.3798 | 1.5422e-06 | 0,47187551159007-3,71422551435309E-08i | 0.47188 | -3.7142e-08 | 0.47188 | -4.5099e-06 | 1.194 | 0.65774 | 15.57% | 1.3155 | 12.0986
200 | 100 | 0 | 1,7035218147927822-1,6670664469104744E-12i | 1.7035 | -1.6671e-12 | 1.7035 | -5.607e-11 | 1,3097251087059678-1,185414425716527E-12i | 1.3097 | -1.1854e-12 | 1.3097 | -5.1858e-11 | 0,39379670608682-4,8165202119395E-13i | 0.3938 | -4.8165e-13 | 0.3938 | -7.0078e-11 | 1.194 | 0.50956 | 9.696% | 1.0191 | 15.6169
250 | 100 | 0 | 1,5863413990796575-1,5355458229197567E-12i | 1.5863 | -1.5355e-12 | 1.5863 | -5.5461e-11 | 1,2470138096519763-1,1251651008707624E-12i | 1.247 | -1.1252e-12 | 1.247 | -5.1697e-11 | 0,33932758942768-4,1038072204899E-13i | 0.33933 | -4.1038e-13 | 0.33933 | -6.9293e-11 | 1.194 | 0.39238 | 4.443% | 0.78476 | 20.2807
300 | 100 | 0 | 1,5349915259991866-4,2080877810358375E-9i | 1.535 | -4.2081e-09 | 1.535 | -1.5707e-07 | 1,2164934275033132-1,0887138294826584E-12i | 1.2165 | -1.0887e-12 | 1.2165 | -5.1277e-11 | 0,31849809849587-4,20699906720635E-09i | 0.3185 | -4.207e-09 | 0.3185 | -7.5681e-07 | 1.194 | 0.34103 | 1.887% | 0.68206 | 23.3344
350 | 100 | 0 | 1,4973701207130838-6,96928338925558E-7i | 1.4974 | -6.9693e-07 | 1.4974 | -2.6667e-05 | 1,1661776905012513-1,9517479193188438E-8i | 1.1662 | -1.9517e-08 | 1.1662 | -9.5892e-07 | 0,33119243021183-6,7741085973237E-07i | 0.33119 | -6.7741e-07 | 0.33119 | -0.00011719 | 1.194 | 0.30341 | -2.327% | 0.60682 | 26.2277
400 | 100 | 0 | 1,4494997172263158-8,393902889053836E-7i | 1.4495 | -8.3939e-07 | 1.4495 | -3.3179e-05 | 1,1426221698861267-1,0248847551188999E-12i | 1.1426 | -1.0249e-12 | 1.1426 | -5.1392e-11 | 0,30687754734019-8,39389264020628E-07i | 0.30688 | -8.3939e-07 | 0.30688 | -0.00015672 | 1.194 | 0.25554 | -4.3% | 0.51108 | 31.141
500 | 100 | 0 | 1,397739929288732-2,429255132521822E-9i | 1.3977 | -2.4293e-09 | 1.3977 | -9.9579e-08 | 1,1226331356679542-1,2178323251642607E-9i | 1.1226 | -1.2178e-09 | 1.1226 | -6.2154e-08 | 0,27510679362078-1,21142280735756E-09i | 0.27511 | -1.2114e-09 | 0.27511 | -2.523e-07 | 1.194 | 0.20378 | -5.974% | 0.40756 | 39.0508
600 | 100 | 0 | 1,3770992824072084-1,3064362911106798E-12i | 1.3771 | -1.3064e-12 | 1.3771 | -5.4356e-11 | 1,1243977756447259-7,433806914650908E-7i | 1.1244 | -7.4338e-07 | 1.1244 | -3.788e-05 | 0,25270150676248+7,43379385028799E-07i | 0.2527 | 7.4338e-07 | 0.2527 | 0.00016855 | 1.194 | 0.18314 | -5.826% | 0.36628 | 43.452
800 | 100 | 0 | 1,3180235407548802-2,1596107618447774E-7i | 1.318 | -2.1596e-07 | 1.318 | -9.388e-06 | 1,0856610332763932-2,2801861003877274E-6i | 1.0857 | -2.2802e-06 | 1.0857 | -0.00012034 | 0,23236250747849+2,06422502420324E-06i | 0.23236 | 2.0642e-06 | 0.23236 | 0.000509 | 1.194 | 0.12406 | -9.071% | 0.24813 | 64.1428
1000 | 100 | 0 | 1,2917199974774372-1,2114690944621413E-12i | 1.2917 | -1.2115e-12 | 1.2917 | -5.3736e-11 | 1,0833718800008103+1,4611654663116683E-6i | 1.0834 | 1.4612e-06 | 1.0834 | 7.7276e-05 | 0,20834811747662-1,46116667778075E-06i | 0.20835 | -1.4612e-06 | 0.20835 | -0.00040182 | 1.194 | 0.097759 | -9.262% | 0.19552 | 81.4013
1500 | 100 | 0 | 1,2859136708665757-3,7971341026451073E-13i | 1.2859 | -3.7971e-13 | 1.2859 | -1.6919e-11 | 1,0736511497027226+2,911836232443757E-13i | 1.0737 | 2.9118e-13 | 1.0737 | 1.5539e-11 | 0,21226252116385-6,70897033508885E-13i | 0.21226 | -6.709e-13 | 0.21226 | -1.8109e-10 | 1.194 | 0.091953 | -10.08% | 0.18391 | 86.5414
10 | 100 | 1572 | 6,478806209378619+0,9681014456205734i | 6.4788 | 0.9681 | 6.5507 | 8.4986 | 5,253402978431903+0,08544524082940404i | 5.2534 | 0.085445 | 5.2541 | 0.93182 | 1,22540323094671+0,882656204791169i | 1.2254 | 0.88266 | 1.5102 | 35.7652 | 1.194 | 5.2454 | 340.1% | 10.4907 | 1.5171
20 | 100 | 1572 | 4,843769633420275+2,0699244634526046i | 4.8438 | 2.0699 | 5.2675 | 23.1388 | 3,5464550360752347+0,10690450801673743i | 3.5465 | 0.1069 | 3.5481 | 1.7266 | 1,29731459734504+1,96301995543586i | 1.2973 | 1.963 | 2.353 | 56.5402 | 1.194 | 3.4949 | 197.2% | 6.9898 | 2.277
30 | 100 | 1572 | 4,183076468286036+3,1859466271642995i | 4.1831 | 3.1859 | 5.2582 | 37.2939 | 2,817286026724784+0,1295624903334628i | 2.8173 | 0.12956 | 2.8203 | 2.6331 | 1,36579044156125+3,05638413683083i | 1.3658 | 3.0564 | 3.3477 | 65.9218 | 1.194 | 2.6989 | 136.2% | 5.3979 | 2.9485
40 | 100 | 1572 | 3,802006908736999+4,271759765739455i | 3.802 | 4.2718 | 5.7187 | 48.3299 | 2,418848483223864+0,1518501792138659i | 2.4188 | 0.15185 | 2.4236 | 3.5922 | 1,38315842551313+4,11990958652559i | 1.3832 | 4.1199 | 4.3459 | 71.4418 | 1.194 | 2.1709 | 103% | 4.3418 | 3.6657
50 | 100 | 1572 | 3,633235121217109+5,352623499119215i | 3.6332 | 5.3526 | 6.4692 | 55.8323 | 2,1653743937087224+0,17534012102158023i | 2.1654 | 0.17534 | 2.1725 | 4.6294 | 1,46786072750838+5,17728337809763i | 1.4679 | 5.1773 | 5.3813 | 74.1709 | 1.194 | 1.8487 | 81.95% | 3.6973 | 4.3046
60 | 100 | 1572 | 3,545590858751401+6,477212005583929i | 3.5456 | 6.4772 | 7.3841 | 61.3039 | 1,9932481862760383+0,1971304822124638i | 1.9932 | 0.19713 | 2.003 | 5.6481 | 1,55234267247537+6,28008152337146i | 1.5523 | 6.2801 | 6.4691 | 76.1157 | 1.194 | 1.6045 | 67.76% | 3.209 | 4.9596
70 | 100 | 1572 | 3,4429631307268598+7,530437138337566i | 3.443 | 7.5304 | 8.2802 | 65.4298 | 1,8782237269865918+0,2179885469697063i | 1.8782 | 0.21799 | 1.8908 | 6.6202 | 1,56473940374026+7,31244859136785i | 1.5647 | 7.3124 | 7.478 | 77.9218 | 1.194 | 1.343 | 58.37% | 2.6861 | 5.9252
80 | 100 | 1572 | 3,5142644877831355+8,467622746894362i | 3.5143 | 8.4676 | 9.1679 | 67.4604 | 1,76538956210423+0,2406509800794729i | 1.7654 | 0.24065 | 1.7817 | 7.7625 | 1,7488749256789+8,22697176681489i | 1.7489 | 8.227 | 8.4108 | 77.9988 | 1.194 | 1.254 | 49.23% | 2.508 | 6.346
90 | 100 | 1572 | 3,573403904453063+9,709390050096268i | 3.5734 | 9.7094 | 10.3461 | 69.7946 | 1,703562420786812+0,2605056578473423i | 1.7036 | 0.26051 | 1.7234 | 8.6942 | 1,86984148366625+9,44888439224892i | 1.8698 | 9.4489 | 9.6321 | 78.8063 | 1.194 | 1.1476 | 44.34% | 2.2952 | 6.9343
100 | 100 | 1572 | 3,5805038554994235+10,428306719702178i | 3.5805 | 10.4283 | 11.0259 | 71.0504 | 1,6331765293498608+0,277721100586479i | 1.6332 | 0.27772 | 1.6566 | 9.6508 | 1,94732732614956+10,1505856191156i | 1.9473 | 10.1506 | 10.3357 | 79.1401 | 1.194 | 0.99224 | 38.75% | 1.9845 | 8.02
150 | 100 | 1572 | 4,076287108074584+15,039418267680375i | 4.0763 | 15.0394 | 15.582 | 74.8349 | 1,491442235662852+0,36618237773180573i | 1.4914 | 0.36618 | 1.5357 | 13.7945 | 2,58484487241173+14,6732358899485i | 2.5848 | 14.6732 | 14.8992 | 80.0093 | 1.194 | 0.65774 | 28.63% | 1.3155 | 12.0986
200 | 100 | 1572 | 4,7659303505012405+19,631944443648653i | 4.7659 | 19.6319 | 20.2022 | 76.3546 | 1,4337698787283866+0,4367889209178006i | 1.4338 | 0.43679 | 1.4988 | 16.943 | 3,33216047177286+19,1951555227308i | 3.3322 | 19.1952 | 19.4822 | 80.1519 | 1.194 | 0.50956 | 25.53% | 1.0191 | 15.6169
250 | 100 | 1572 | 5,521401641555291+24,726933123425223i | 5.5214 | 24.7269 | 25.3359 | 77.4126 | 1,4220553551938286+0,47528697600408915i | 1.4221 | 0.47529 | 1.4994 | 18.4809 | 4,09934628636147+24,2516461474211i | 4.0993 | 24.2516 | 24.5957 | 80.4058 | 1.194 | 0.39238 | 25.58% | 0.78476 | 20.2807
300 | 100 | 1572 | 6,288889582855006+28,792347563931497i | 6.2889 | 28.7923 | 29.4712 | 77.6788 | 1,4313086540855264+0,4930283126320041i | 1.4313 | 0.49303 | 1.5138 | 19.0068 | 4,85758092876948+28,2993192512994i | 4.8576 | 28.2993 | 28.7132 | 80.2601 | 1.194 | 0.34103 | 26.79% | 0.68206 | 23.3344
350 | 100 | 1572 | 7,060247602363399+30,485786717729596i | 7.0602 | 30.4858 | 31.2927 | 76.9607 | 1,4484582643781985+0,5034711235558466i | 1.4485 | 0.50347 | 1.5335 | 19.167 | 5,6117893379852+29,9823155941737i | 5.6118 | 29.9823 | 30.503 | 79.3986 | 1.194 | 0.30341 | 28.44% | 0.60682 | 26.2277
400 | 100 | 1572 | 7,819596808231986+34,336473294407526i | 7.8196 | 34.3365 | 35.2156 | 77.1706 | 1,4355853433188257+0,5033733925369858i | 1.4356 | 0.50337 | 1.5213 | 19.3227 | 6,38401146491316+33,8330999018705i | 6.384 | 33.8331 | 34.4301 | 79.3144 | 1.194 | 0.25554 | 27.41% | 0.51108 | 31.141
500 | 100 | 1572 | 9,332474023813887+40,48835746769328i | 9.3325 | 40.4884 | 41.55 | 77.0202 | 1,4491137306840676+0,499998443199567i | 1.4491 | 0.5 | 1.5329 | 19.0363 | 7,88336029312982+39,9883590244936i | 7.8834 | 39.9884 | 40.758 | 78.8476 | 1.194 | 0.20378 | 28.39% | 0.40756 | 39.0508
600 | 100 | 1572 | 10,839524789873854+48,537371820076046i | 10.8395 | 48.5374 | 49.733 | 77.4111 | 1,4358867050323745+0,5036509436119322i | 1.4359 | 0.50365 | 1.5217 | 19.3288 | 9,40363808484143+48,0337208764641i | 9.4036 | 48.0337 | 48.9455 | 78.9232 | 1.194 | 0.18314 | 27.45% | 0.36628 | 43.452
800 | 100 | 1572 | 13,668778537964458+56,87887803831912i | 13.6688 | 56.8789 | 58.4982 | 76.4873 | 1,4439215289104856+0,4982207748790701i | 1.4439 | 0.49822 | 1.5275 | 19.0368 | 12,2248570090539+56,38065726344i | 12.2249 | 56.3807 | 57.6908 | 77.7661 | 1.194 | 0.12406 | 27.93% | 0.24813 | 64.1428
1000 | 100 | 1572 | 16,607120189567848+67,65120578361415i | 16.6071 | 67.6512 | 69.6598 | 76.2077 | 1,4570621065586689+0,5081454666421124i | 1.4571 | 0.50815 | 1.5431 | 19.226 | 15,1500580830091+67,143060316972i | 15.1501 | 67.1431 | 68.8311 | 77.2848 | 1.194 | 0.097759 | 29.24% | 0.19552 | 81.4013
1500 | 100 | 1572 | 24,388060008238234+117,8507927715579i | 24.3881 | 117.8508 | 120.3478 | 78.3082 | 1,4621+0,50576i | 1.4621 | 0.50576 | 1.5471 | 19.0812 | 22,9259600082382+117,345032771557i | 22.926 | 117.345 | 119.5636 | 78.9452 | 1.194 | 0.091953 | 29.58% | 0.18391 | 86.5414
10 | 300 | 0 | 19,317988806711885-5,204970396617918E-11i | 19.318 | -5.205e-11 | 19.318 | -1.5438e-10 | 15,669849836887261-3,9859658642103056E-11i | 15.6698 | -3.986e-11 | 15.6698 | -1.4574e-10 | 3,6481389698246-1,21900453240761E-11i | 3.6481 | -1.219e-11 | 3.6481 | -1.9145e-10 | 3.5819 | 15.7361 | 337.5% | 31.4722 | 1.5171
20 | 300 | 0 | 14,066509152166425-3,943539898612689E-11i | 14.0665 | -3.9435e-11 | 14.0665 | -1.6063e-10 | 10,61315289141024-2,7671631047873825E-11i | 10.6132 | -2.7672e-11 | 10.6132 | -1.4939e-10 | 3,4533562607562-1,1763767938253E-11i | 3.4534 | -1.1764e-11 | 3.4534 | -1.9518e-10 | 3.5819 | 10.4846 | 196.3% | 20.9693 | 2.277
30 | 300 | 0 | 11,678724329979438-3,336206698623239E-11i | 11.6787 | -3.3362e-11 | 11.6787 | -1.6367e-10 | 8,416964767617683-2,222707168295412E-11i | 8.417 | -2.2227e-11 | 8.417 | -1.513e-10 | 3,26175956236172-1,11349953032782E-11i | 3.2618 | -1.1135e-11 | 3.2618 | -1.956e-10 | 3.5819 | 8.0968 | 135% | 16.1937 | 2.9485
40 | 300 | 0 | 10,094546044332189-2,939435872717265E-11i | 10.0945 | -2.9394e-11 | 10.0945 | -1.6684e-10 | 7,191977685311562-1,9195773447262045E-11i | 7.192 | -1.9196e-11 | 7.192 | -1.5293e-10 | 2,90256835902054-1,01985852799106E-11i | 2.9026 | -1.0199e-11 | 2.9026 | -2.0132e-10 | 3.5819 | 6.5127 | 100.8% | 13.0253 | 3.6657
50 | 300 | 0 | 9,127920348692184-2,6687880000026177E-11i | 9.1279 | -2.6688e-11 | 9.1279 | -1.6752e-10 | 6,420303647791297-1,7187843777450294E-11i | 6.4203 | -1.7188e-11 | 6.4203 | -1.5339e-10 | 2,70761670090089-9,5000362225759E-12i | 2.7076 | -9.5e-12 | 2.7076 | -2.0103e-10 | 3.5819 | 5.546 | 79.24% | 11.0921 | 4.3046
60 | 300 | 0 | 8,395355306482367-2,4566129024774748E-11i | 8.3954 | -2.4566e-11 | 8.3954 | -1.6766e-10 | 5,900974578321671-1,5943461204961022E-11i | 5.901 | -1.5943e-11 | 5.901 | -1.548e-10 | 2,49438072816069-8,6226678198137E-12i | 2.4944 | -8.6227e-12 | 2.4944 | -1.9806e-10 | 3.5819 | 4.8135 | 64.75% | 9.6269 | 4.9597
70 | 300 | 0 | 7,610989678075101-2,2292235451115438E-11i | 7.611 | -2.2292e-11 | 7.611 | -1.6782e-10 | 5,558163190583664+2,2634454488387897E-9i | 5.5582 | 2.2634e-09 | 5.5582 | 2.3333e-08 | 2,05282648749144-2,2857376842899E-09i | 2.0528 | -2.2857e-09 | 2.0528 | -6.3796e-08 | 3.5819 | 4.0291 | 55.17% | 8.0582 | 5.9252
80 | 300 | 0 | 7,343826058231102-9,024494220353322E-7i | 7.3438 | -9.0245e-07 | 7.3438 | -7.0408e-06 | 5,236200922893058-1,4167045013096573E-11i | 5.2362 | -1.4167e-11 | 5.2362 | -1.5502e-10 | 2,10762513533805-9,02435254990319E-07i | 2.1076 | -9.0244e-07 | 2.1076 | -2.4533e-05 | 3.5819 | 3.7619 | 46.19% | 7.5239 | 6.346
90 | 300 | 0 | 7,024671330159731-2,0521955548906012E-11i | 7.0247 | -2.0522e-11 | 7.0247 | -1.6738e-10 | 4,970523036427225-1,3437223856953255E-11i | 4.9705 | -1.3437e-11 | 4.9705 | -1.5489e-10 | 2,05414829373251-7,0847316919528E-12i | 2.0541 | -7.0847e-12 | 2.0541 | -1.9761e-10 | 3.5819 | 3.4428 | 38.77% | 6.8856 | 6.9343
100 | 300 | 0 | 6,558605180570382+6,062283560965955E-10i | 6.5586 | 6.0623e-10 | 6.5586 | 5.296e-09 | 4,781693245586738-1,304840384374274E-11i | 4.7817 | -1.3048e-11 | 4.7817 | -1.5635e-10 | 1,77691193498365+6,19276759940338E-10i | 1.7769 | 6.1928e-10 | 1.7769 | 1.9968e-08 | 3.5819 | 2.9767 | 33.5% | 5.9534 | 8.02
150 | 300 | 0 | 5,555115952748428-1,6284095237546077E-11i | 5.5551 | -1.6284e-11 | 5.5551 | -1.6796e-10 | 4,139458144474791-2,120542504618705E-11i | 4.1395 | -2.1205e-11 | 4.1395 | -2.9351e-10 | 1,41565780827363+4,921329808641E-12i | 1.4157 | 4.9213e-12 | 1.4157 | 1.9918e-10 | 3.5819 | 1.9732 | 15.57% | 3.9465 | 12.0985
200 | 300 | 0 | 5,110565504777665-1,4966977427586613E-11i | 5.1106 | -1.4967e-11 | 5.1106 | -1.678e-10 | 3,929171421715715-1,0656356691160172E-11i | 3.9292 | -1.0656e-11 | 3.9292 | -1.5539e-10 | 1,18139408306195-4,3106207364265E-12i | 1.1814 | -4.3106e-12 | 1.1814 | -2.0906e-10 | 3.5819 | 1.5287 | 9.696% | 3.0574 | 15.6169
250 | 300 | 0 | 4,759031485953721-1,4139606911683837E-11i | 4.759 | -1.414e-11 | 4.759 | -1.7023e-10 | 3,741040573613424-1,0126597676301581E-11i | 3.741 | -1.0127e-11 | 3.741 | -1.5509e-10 | 1,0179909123403-4,0130092353823E-12i | 1.018 | -4.013e-12 | 1.018 | -2.2586e-10 | 3.5819 | 1.1771 | 4.443% | 2.3543 | 20.2805
300 | 300 | 0 | 4,604941485949752-1,3340313913455291E-11i | 4.6049 | -1.334e-11 | 4.6049 | -1.6598e-10 | 3,6494991092179268-6,357212631418414E-12i | 3.6495 | -6.3572e-12 | 3.6495 | -9.9806e-11 | 0,95544237673183-6,98310128203679E-12i | 0.95544 | -6.9831e-12 | 0.95544 | -4.1876e-10 | 3.5819 | 1.0231 | 1.888% | 2.0461 | 23.3351
350 | 300 | 0 | 4,492118754130296-1,293382104410048E-11i | 4.4921 | -1.2934e-11 | 4.4921 | -1.6497e-10 | 3,4985208692224736-1,801229311074432E-11i | 3.4985 | -1.8012e-11 | 3.4985 | -2.9499e-10 | 0,99359788490782+5,0784720666439E-12i | 0.9936 | 5.0785e-12 | 0.9936 | 2.9285e-10 | 3.5819 | 0.91024 | -2.327% | 1.8205 | 26.2275
400 | 300 | 0 | 4,348500530547389-1,006134354566613E-11i | 4.3485 | -1.0061e-11 | 4.3485 | -1.3257e-10 | 3,4278886877875516-9,001356084686806E-12i | 3.4279 | -9.0014e-12 | 3.4279 | -1.5045e-10 | 0,92061184275983-1,0599874609793E-12i | 0.92061 | -1.06e-12 | 0.92061 | -6.597e-11 | 3.5819 | 0.76662 | -4.299% | 1.5332 | 31.141
500 | 300 | 0 | 4,193218350714471+1,1997027581551203E-6i | 4.1932 | 1.1997e-06 | 4.1932 | 1.6393e-05 | 3,367912686249142+2,8436980261258223E-6i | 3.3679 | 2.8437e-06 | 3.3679 | 4.8378e-05 | 0,82530566446533-0,0000016439952679707i | 0.82531 | -1.644e-06 | 0.82531 | -0.00011413 | 3.5819 | 0.61134 | -5.974% | 1.2227 | 39.0509
600 | 300 | 0 | 4,131303112375405-1,174047845572484E-11i | 4.1313 | -1.174e-11 | 4.1313 | -1.6283e-10 | 3,373198754246196-9,939913386670847E-12i | 3.3732 | -9.9399e-12 | 3.3732 | -1.6884e-10 | 0,75810435812921-1,80056506905396E-12i | 0.7581 | -1.8006e-12 | 0.7581 | -1.3608e-10 | 3.5819 | 0.54942 | -5.826% | 1.0988 | 43.4516
800 | 300 | 0 | 3,9540641379613355+1,2591532173334866E-6i | 3.9541 | 1.2592e-06 | 3.9541 | 1.8246e-05 | 3,2569872047416855-1,0579865672301877E-10i | 3.257 | -1.058e-10 | 3.257 | -1.8612e-09 | 0,69707693321965+0,0000012592590159902i | 0.69708 | 1.2593e-06 | 0.69708 | 0.0001035 | 3.5819 | 0.37218 | -9.07% | 0.74436 | 64.1439
1000 | 300 | 0 | 3,875171817982547+2,1324262735975893E-11i | 3.8752 | 2.1324e-11 | 3.8752 | 3.1529e-10 | 3,250123759926246-8,679518645648317E-12i | 3.2501 | -8.6795e-12 | 3.2501 | -1.5301e-10 | 0,6250480580563+3,00037813816241E-11i | 0.62505 | 3.0004e-11 | 0.62505 | 2.7503e-09 | 3.5819 | 0.29329 | -9.262% | 0.58658 | 81.398
1500 | 300 | 0 | 3,8577366593402793-1,7927524936712235E-5i | 3.8577 | -1.7928e-05 | 3.8577 | -0.00026626 | 3,220944354476896-5,6483115220112485E-12i | 3.2209 | -5.6483e-12 | 3.2209 | -1.0048e-10 | 0,63679230486338-0,0000179275192884007i | 0.63679 | -1.7928e-05 | 0.63679 | -0.001613 | 3.5819 | 0.27585 | -10.08% | 0.55171 | 86.5427
10 | 300 | 1572 | 19,296522719785944+1,001215831806404i | 19.2965 | 1.0012 | 19.3225 | 2.9702 | 15,75456187376434+0,0859773406575419i | 15.7546 | 0.085977 | 15.7548 | 0.31268 | 3,5419608460216+0,915238491148858i | 3.542 | 0.91524 | 3.6583 | 14.4883 | 3.5819 | 15.7361 | 339.8% | 31.4722 | 1.5171
20 | 300 | 1572 | 14,155224742925107+2,1607343449850656i | 14.1552 | 2.1607 | 14.3192 | 8.679 | 10,632529428805395+0,1076099887830747i | 10.6325 | 0.10761 | 10.6331 | 0.57986 | 3,5226953141198+2,05312435620199i | 3.5227 | 2.0531 | 4.0773 | 30.2348 | 3.5819 | 10.4846 | 196.9% | 20.9693 | 2.277
30 | 300 | 1572 | 11,877111128783577+3,3599159373896796i | 11.8771 | 3.3599 | 12.3432 | 15.7957 | 8,442430064819819+0,1306078765154238i | 8.4424 | 0.13061 | 8.4434 | 0.88632 | 3,43468106396369+3,22930806087425i | 3.4347 | 3.2293 | 4.7144 | 43.2348 | 3.5819 | 8.0968 | 135.7% | 16.1937 | 2.9485
40 | 300 | 1572 | 10,416826425180655+4,5443186424587685i | 10.4168 | 4.5443 | 11.3649 | 23.5691 | 7,243322360659091+0,15332934425776168i | 7.2433 | 0.15333 | 7.2449 | 1.2127 | 3,17350406452151+4,390989298201i | 3.1735 | 4.391 | 5.4177 | 54.1432 | 3.5819 | 6.5127 | 102.3% | 13.0253 | 3.6657
50 | 300 | 1572 | 9,585497131212033+5,731436361264451i | 9.5855 | 5.7314 | 11.1683 | 30.8764 | 6,477476298721472+0,17738756321047158i | 6.4775 | 0.17739 | 6.4799 | 1.5687 | 3,10802083249056+5,55404879805398i | 3.108 | 5.554 | 6.3645 | 60.7688 | 3.5819 | 5.546 | 80.91% | 11.0921 | 4.3046
60 | 300 | 1572 | 8,995679648858399+6,965325347333152i | 8.9957 | 6.9653 | 11.3771 | 37.7505 | 5,954519344634563+0,19985446317412237i | 5.9545 | 0.19985 | 5.9579 | 1.9223 | 3,04116030422383+6,76547088415903i | 3.0412 | 6.7655 | 7.4176 | 65.7955 | 3.5819 | 4.8135 | 66.33% | 9.6269 | 4.9597
70 | 300 | 1572 | 8,359265946000916+8,12962625071709i | 8.3593 | 8.1296 | 11.6605 | 44.2021 | 5,6013380557999435+0,22154760211200028i | 5.6013 | 0.22155 | 5.6057 | 2.265 | 2,75792789020097+7,90807864860509i | 2.7579 | 7.9081 | 8.3752 | 70.7739 | 3.5819 | 4.0291 | 56.5% | 8.0582 | 5.9252
80 | 300 | 1572 | 8,24305150419584+9,178031834945214i | 8.2431 | 9.178 | 12.3363 | 48.0721 | 5,252083322126+0,2453773351800154i | 5.2521 | 0.24538 | 5.2578 | 2.6749 | 2,99096818206984+8,9326544997652i | 2.991 | 8.9327 | 9.4201 | 71.4876 | 3.5819 | 3.7619 | 46.79% | 7.5239 | 6.346
90 | 300 | 1572 | 8,078899988365839+10,532545161847478i | 8.0789 | 10.5325 | 13.2742 | 52.5103 | 5,05482503848165+0,26654409511987853i | 5.0548 | 0.26654 | 5.0618 | 3.0184 | 3,02407494988418+10,2660010667275i | 3.0241 | 10.266 | 10.7021 | 73.5865 | 3.5819 | 3.4428 | 41.32% | 6.8856 | 6.9343
100 | 300 | 1572 | 7,7678222235772+11,363767471216828i | 7.7678 | 11.3638 | 13.765 | 55.645 | 4,831525873928045+0,2852818813336013i | 4.8315 | 0.28528 | 4.8399 | 3.3792 | 2,93629634964916+11,0784855898832i | 2.9363 | 11.0785 | 11.461 | 75.1554 | 3.5819 | 2.9767 | 35.12% | 5.9534 | 8.02
150 | 300 | 1572 | 7,556970138830201+16,546233852865047i | 7.557 | 16.5462 | 18.1903 | 65.4529 | 4,315333536932442+0,3876447212068899i | 4.3153 | 0.38764 | 4.3327 | 5.1331 | 3,24163660189776+16,1585891316581i | 3.2416 | 16.1586 | 16.4805 | 78.6563 | 3.5819 | 1.9732 | 20.96% | 3.9465 | 12.0985
200 | 300 | 1572 | 7,9200255590914574+21,724007956489412i | 7.92 | 21.724 | 23.1227 | 69.9694 | 4,013102779148411+0,4880333943912193i | 4.0131 | 0.48803 | 4.0427 | 6.9337 | 3,90692277994304+21,2359745620982i | 3.9069 | 21.236 | 21.5924 | 79.5755 | 3.5819 | 1.5287 | 12.86% | 3.0574 | 15.6169
250 | 300 | 1572 | 8,414636503506678+27,45040752768238i | 8.4146 | 27.4504 | 28.7112 | 72.9576 | 3,8618307326055548+0,567441269716608i | 3.8618 | 0.56744 | 3.9033 | 8.359 | 4,55280577090112+26,8829662579657i | 4.5528 | 26.883 | 27.2658 | 80.3878 | 3.5819 | 1.1771 | 8.973% | 2.3543 | 20.2805
300 | 300 | 1572 | 9,081815173006072+32,10941233822368i | 9.0818 | 32.1094 | 33.3691 | 74.207 | 3,7912503452048423+0,6357420248577749i | 3.7913 | 0.63574 | 3.8442 | 9.5192 | 5,29056482780123+31,4736703133658i | 5.2906 | 31.4737 | 31.9152 | 80.4581 | 3.5819 | 1.0231 | 7.323% | 2.0461 | 23.3351
350 | 300 | 1572 | 9,808836951937337+34,41357512584889i | 9.8088 | 34.4136 | 35.7842 | 74.091 | 3,768310167123551+0,7043545999474204i | 3.7683 | 0.70435 | 3.8336 | 10.5873 | 6,04052678481378+33,7092205259014i | 6.0405 | 33.7092 | 34.2462 | 79.8407 | 3.5819 | 0.91024 | 7.027% | 1.8205 | 26.2275
400 | 300 | 1572 | 10,521721843317964+38,86888949440673i | 10.5217 | 38.8689 | 40.2678 | 74.8532 | 3,7299217451655386+0,7257032144582095i | 3.7299 | 0.7257 | 3.7999 | 11.0101 | 6,79180009815237+38,1431862799485i | 6.7918 | 38.1432 | 38.7431 | 79.9037 | 3.5819 | 0.76662 | 6.086% | 1.5332 | 31.141
500 | 300 | 1572 | 12,059555233398257+46,16845353572832i | 12.0596 | 46.1685 | 47.7175 | 75.361 | 3,751216746761504+0,7926352858142194i | 3.7512 | 0.79264 | 3.834 | 11.9311 | 8,3083384866367+45,3758182499141i | 8.3083 | 45.3758 | 46.1302 | 79.624 | 3.5819 | 0.61134 | 7.04% | 1.2227 | 39.0509
600 | 300 | 1572 | 13,610705198902899+55,28577837179415i | 13.6107 | 55.2858 | 56.9365 | 76.1695 | 3,732311765582198+0,797316593167052i | 3.7323 | 0.79732 | 3.8165 | 12.0586 | 9,87839343332061+54,488461778627i | 9.8784 | 54.4885 | 55.3767 | 79.7243 | 3.5819 | 0.54942 | 6.551% | 1.0988 | 43.4516
800 | 300 | 1572 | 16,444910510463323+65,68729013330739i | 16.4449 | 65.6873 | 67.7145 | 75.9448 | 3,767825342100446+0,8052124530081848i | 3.7678 | 0.80521 | 3.8529 | 12.0631 | 12,6770851683629+64,8820776802991i | 12.6771 | 64.8821 | 66.1089 | 78.9445 | 3.5819 | 0.37218 | 7.566% | 0.74436 | 64.1439
1000 | 300 | 1572 | 19,53942764993717+78,66153471718133i | 19.5394 | 78.6615 | 81.052 | 76.0501 | 3,7725552200449455+0,830315934855076i | 3.7726 | 0.83032 | 3.8628 | 12.4125 | 15,7668724298922+77,8312187823262i | 15.7669 | 77.8312 | 79.4122 | 78.5481 | 3.5819 | 0.29329 | 7.844% | 0.58658 | 81.398
1500 | 300 | 1572 | 27,16671645578161+134,24983074847404i | 27.1667 | 134.2498 | 136.971 | 78.5601 | 3,7916+0,8305i | 3.7916 | 0.8305 | 3.8815 | 12.3548 | 23,3751164557816+133,419330748474i | 23.3751 | 133.4193 | 135.4515 | 80.0626 | 3.5819 | 0.27585 | 8.365% | 0.55171 | 86.5427
10 | 5252 | 0 | 338,19358681895136-1,5952368737697145E-8i | 338.1936 | -1.5952e-08 | 338.1936 | -2.7026e-09 | 274,3268395957924-1,2216323630621524E-8i | 274.3268 | -1.2216e-08 | 274.3268 | -2.5515e-09 | 63,866747223159-3,7360451070756E-09i | 63.8667 | -3.736e-09 | 63.8667 | -3.3517e-09 | 62.7068 | 275.4868 | 337.5% | 550.9736 | 1.5171
20 | 5252 | 0 | 246,2581426186062-1,2086413356406415E-8i | 246.2581 | -1.2086e-08 | 246.2581 | -2.8121e-09 | 185,80092928203982-8,480895026615095E-9i | 185.8009 | -8.4809e-09 | 185.8009 | -2.6153e-09 | 60,457213336567-3,60551832979131E-09i | 60.4572 | -3.6055e-09 | 60.4572 | -3.417e-09 | 62.7068 | 183.5513 | 196.3% | 367.1027 | 2.277
30 | 5252 | 0 | 204,4554388527994-1,0224878243714381E-8i | 204.4554 | -1.0225e-08 | 204.4554 | -2.8654e-09 | 147,35292813902214-6,812197640114265E-9i | 147.3529 | -6.8122e-09 | 147.3529 | -2.6488e-09 | 57,102510713777-3,41268060360004E-09i | 57.1025 | -3.4127e-09 | 57.1025 | -3.4242e-09 | 62.7068 | 141.7486 | 135% | 283.4973 | 2.9485
40 | 5252 | 0 | 176,7221178811223-9,007938826887913E-9i | 176.7221 | -9.0079e-09 | 176.7221 | -2.9205e-09 | 125,9075539333185-5,88318582440721E-9i | 125.9076 | -5.8832e-09 | 125.9076 | -2.6772e-09 | 50,814563947804-3,1247530024807E-09i | 50.8146 | -3.1248e-09 | 50.8146 | -3.5233e-09 | 62.7068 | 114.0153 | 100.8% | 228.0306 | 3.6657
50 | 5252 | 0 | 159,79888551918853-8,1920463658924E-9i | 159.7989 | -8.192e-09 | 159.7989 | -2.9373e-09 | 112,3981215457141-5,267788190696338E-9i | 112.3981 | -5.2678e-09 | 112.3981 | -2.6853e-09 | 47,400763973474-2,92425817519607E-09i | 47.4008 | -2.9243e-09 | 47.4008 | -3.5347e-09 | 62.7068 | 97.0921 | 79.24% | 194.1842 | 4.3046
60 | 5252 | 0 | 146,9750535243905-7,52919034242783E-9i | 146.9751 | -7.5292e-09 | 146.9751 | -2.9351e-09 | 103,30639561254529-4,886407092393737E-9i | 103.3064 | -4.8864e-09 | 103.3064 | -2.7101e-09 | 43,668657911845-2,6427832500341E-09i | 43.6687 | -2.6428e-09 | 43.6687 | -3.4675e-09 | 62.7068 | 84.2682 | 64.75% | 168.5365 | 4.9596
70 | 5252 | 0 | 133,24320191030546-1,4272779903839175E-5i | 133.2432 | -1.4273e-05 | 133.2432 | -6.1374e-06 | 97,30486911985003-4,600698587503911E-9i | 97.3049 | -4.6007e-09 | 97.3049 | -2.709e-09 | 35,938332790455-0,0000142681792052516i | 35.9383 | -1.4268e-05 | 35.9383 | -2.2747e-05 | 62.7068 | 70.5364 | 55.17% | 141.0728 | 5.9252
80 | 5252 | 0 | 128,56644535827084-3,37330026957125E-4i | 128.5664 | -0.00033733 | 128.5664 | -0.00015033 | 91,66832791979375-4,341957940348319E-9i | 91.6683 | -4.342e-09 | 91.6683 | -2.7139e-09 | 36,8981174384763-0,000337325684999185i | 36.8981 | -0.00033733 | 36.8981 | -0.0005238 | 62.7068 | 65.8596 | 46.19% | 131.7193 | 6.3459
90 | 5252 | 0 | 122,97873477375067-6,289853228191779E-9i | 122.9787 | -6.2899e-09 | 122.9787 | -2.9304e-09 | 87,01725010330203-4,118289691585371E-9i | 87.0173 | -4.1183e-09 | 87.0173 | -2.7117e-09 | 35,961484670448-2,1715635366064E-09i | 35.9615 | -2.1716e-09 | 35.9615 | -3.4599e-09 | 62.7068 | 60.2719 | 38.77% | 120.5439 | 6.9343
100 | 5252 | 0 | 114,81956435901262+1,5697796115894796E-4i | 114.8196 | 0.00015698 | 114.8196 | 7.8333e-05 | 83,71131258137683-3,999133311979196E-9i | 83.7113 | -3.9991e-09 | 83.7113 | -2.7372e-09 | 31,1082517776352+0,000156981960292259i | 31.1083 | 0.00015698 | 31.1083 | 0.00028913 | 62.7068 | 52.1128 | 33.5% | 104.2255 | 8.0199
150 | 5252 | 0 | 97,25155588337194-4,988100846508232E-9i | 97.2516 | -4.9881e-09 | 97.2516 | -2.9387e-09 | 72,46837483120986-3,4832815565498933E-9i | 72.4684 | -3.4833e-09 | 72.4684 | -2.754e-09 | 24,7831810521621-1,50481928995834E-09i | 24.7832 | -1.5048e-09 | 24.7832 | -3.479e-09 | 62.7068 | 34.5447 | 15.57% | 69.0895 | 12.0985
200 | 5252 | 0 | 89,46910813585389-1,4539163762786943E-4i | 89.4691 | -0.00014539 | 89.4691 | -9.3108e-05 | 68,78684965442648-3,26954517354023E-9i | 68.7868 | -3.2695e-09 | 68.7868 | -2.7234e-09 | 20,6822584814274-0,000145388368082695i | 20.6823 | -0.00014539 | 20.6823 | -0.00040277 | 62.7068 | 26.7623 | 9.696% | 53.5246 | 15.6168
250 | 5252 | 0 | 83,31467488596095-6,9460287248205145E-6i | 83.3147 | -6.946e-06 | 83.3147 | -4.7768e-06 | 65,49312559751966-3,1033565779951553E-9i | 65.4931 | -3.1034e-09 | 65.4931 | -2.7149e-09 | 17,8215492884413-6,94292536824252E-06i | 17.8215 | -6.9429e-06 | 17.8215 | -2.2321e-05 | 62.7068 | 20.6079 | 4.443% | 41.2157 | 20.2806
300 | 5252 | 0 | 80,61774799415701-4,082157761428636E-9i | 80.6177 | -4.0822e-09 | 80.6177 | -2.9012e-09 | 63,89017261631343-3,351650273717087E-7i | 63.8902 | -3.3517e-07 | 63.8902 | -3.0057e-07 | 16,7275753778436+3,31082869610279E-07i | 16.7276 | 3.3108e-07 | 16.7276 | 1.134e-06 | 62.7068 | 17.9109 | 1.887% | 35.8219 | 23.3344
350 | 5252 | 0 | 78,64220678799921-3,937055461700752E-9i | 78.6422 | -3.9371e-09 | 78.6422 | -2.8684e-09 | 61,24760515467263-1,1597610459076419E-7i | 61.2476 | -1.1598e-07 | 61.2476 | -1.0849e-07 | 17,3946016333266+1,12039049129063E-07i | 17.3946 | 1.1204e-07 | 17.3946 | 3.6904e-07 | 62.7068 | 15.9354 | -2.327% | 31.8708 | 26.2272
400 | 5252 | 0 | 76,12786362327392+9,03716825312347E-5i | 76.1279 | 9.0372e-05 | 76.1279 | 6.8016e-05 | 60,01083272044655-2,8260632036073175E-9i | 60.0108 | -2.8261e-09 | 60.0108 | -2.6982e-09 | 16,1170309028274+0,0000903745085944383i | 16.117 | 9.0375e-05 | 16.117 | 0.00032128 | 62.7068 | 13.4211 | -4.299% | 26.8421 | 31.1407
500 | 5252 | 0 | 73,4093021155845-3,670220883194205E-9i | 73.4093 | -3.6702e-09 | 73.4093 | -2.8646e-09 | 58,960803012291265-2,762692635803357E-9i | 58.9608 | -2.7627e-09 | 58.9608 | -2.6847e-09 | 14,4484991032933-9,0752824739085E-10i | 14.4485 | -9.0753e-10 | 14.4485 | -3.5988e-09 | 62.7068 | 10.7025 | -5.974% | 21.405 | 39.0508
600 | 5252 | 0 | 72,325257972435-1,212838318414108E-8i | 72.3253 | -1.2128e-08 | 72.3253 | -9.6081e-09 | 59,05338074823818-2,772436858505004E-9i | 59.0534 | -2.7724e-09 | 59.0534 | -2.6899e-09 | 13,2718772241969-9,355946325636E-09i | 13.2719 | -9.3559e-09 | 13.2719 | -4.039e-08 | 62.7068 | 9.6184 | -5.826% | 19.2369 | 43.452
800 | 5252 | 0 | 69,22230647710444+1,7555309701265686E-4i | 69.2223 | 0.00017555 | 69.2223 | 0.00014531 | 57,01876855179976-2,6759782568267757E-9i | 57.0188 | -2.676e-09 | 57.0188 | -2.689e-09 | 12,2035379253047+0,000175555772990913i | 12.2035 | 0.00017556 | 12.2035 | 0.00082424 | 62.7068 | 6.5155 | -9.071% | 13.031 | 64.1457
1000 | 5252 | 0 | 67,84126009539385+8,815799984984703E-5i | 67.8413 | 8.8158e-05 | 67.8413 | 7.4454e-05 | 56,89872747357911+7,010197186112239E-9i | 56.8987 | 7.0102e-09 | 56.8987 | 7.0591e-09 | 10,9425326218147+0,0000881509896526609i | 10.9425 | 8.8151e-05 | 10.9425 | 0.00046156 | 62.7068 | 5.1345 | -9.262% | 10.2689 | 81.3993
1500 | 5252 | 0 | 67,53603623764286-3,328380708349423E-9i | 67.536 | -3.3284e-09 | 67.536 | -2.8237e-09 | 56,38857810044997-4,77572163219587E-5i | 56.3886 | -4.7757e-05 | 56.3886 | -4.8526e-05 | 11,1474581371929+0,0000477538879412504i | 11.1475 | 4.7754e-05 | 11.1475 | 0.00024545 | 62.7068 | 4.8292 | -10.08% | 9.6585 | 86.544
10 | 5252 | 1572 | 336,90282720039363+0,8071013791614621i | 336.9028 | 0.8071 | 336.9038 | 0.13726 | 275,77921163211096-0,10626971425530586i | 275.7792 | -0.10627 | 275.7792 | -0.022079 | 61,123615568283+0,913371093416767i | 61.1236 | 0.91337 | 61.1304 | 0.85611 | 62.7068 | 275.4868 | 339.8% | 550.9736 | 1.5171
20 | 5252 | 1572 | 245,76011220058672+2,1045789511521407i | 245.7601 | 2.1046 | 245.7691 | 0.49064 | 186,11171350531293-0,025963397805412923i | 186.1117 | -0.025963 | 186.1117 | -0.007993 | 59,648398695274+2,13054234895755i | 59.6484 | 2.1305 | 59.6864 | 2.0456 | 62.7068 | 183.5513 | 196.8% | 367.1027 | 2.277
30 | 5252 | 1572 | 204,20621696339387+3,4409735827506993i | 204.2062 | 3.441 | 204.2352 | 0.96537 | 147,76265858602517+0,023426929747599797i | 147.7627 | 0.023427 | 147.7627 | 0.0090839 | 56,443558377368+3,41754665300309i | 56.4436 | 3.4175 | 56.5469 | 3.4649 | 62.7068 | 141.7486 | 135.6% | 283.4973 | 2.9485
40 | 5252 | 1572 | 176,61712412319346+4,780707016200389i | 176.6171 | 4.7807 | 176.6818 | 1.5505 | 126,75827187590002+0,06091921279034147i | 126.7583 | 0.060919 | 126.7583 | 0.027536 | 49,858852247293+4,71978780341004i | 49.8589 | 4.7198 | 50.0817 | 5.4077 | 62.7068 | 114.0153 | 102.1% | 228.0306 | 3.6657
50 | 5252 | 1572 | 159,80469968139468+6,143477359724358i | 159.8047 | 6.1435 | 159.9227 | 2.2016 | 113,33401908575365+0,09426916332793486i | 113.334 | 0.094269 | 113.3341 | 0.047658 | 46,470680595641+6,04920819639641i | 46.4707 | 6.0492 | 46.8627 | 7.4166 | 62.7068 | 97.0921 | 80.74% | 194.1842 | 4.3046
60 | 5252 | 1572 | 147,08015919028796+7,57287467008847i | 147.0802 | 7.5729 | 147.275 | 2.9474 | 104,15864145004186+0,12423223866895265i | 104.1586 | 0.12423 | 104.1587 | 0.068338 | 42,921517740246+7,44864243141952i | 42.9215 | 7.4486 | 43.563 | 9.8451 | 62.7068 | 84.2682 | 66.1% | 168.5365 | 4.9596
70 | 5252 | 1572 | 133,44295989985682+8,953541875915496i | 133.443 | 8.9535 | 133.743 | 3.8386 | 97,95123745084155+0,15091663413669976i | 97.9512 | 0.15092 | 97.9514 | 0.088277 | 35,4917224490145+8,80262524177879i | 35.4917 | 8.8026 | 36.567 | 13.9294 | 62.7068 | 70.5364 | 56.21% | 141.0728 | 5.9252
80 | 5252 | 1572 | 128,86104004250848+10,226418486295447i | 128.861 | 10.2264 | 129.2662 | 4.5375 | 91,8046102850394+0,17952970839532628i | 91.8046 | 0.17953 | 91.8048 | 0.11205 | 37,0564297574686+10,0468887779001i | 37.0564 | 10.0469 | 38.3943 | 15.1696 | 62.7068 | 65.8596 | 46.4% | 131.7193 | 6.3459
90 | 5252 | 1572 | 123,37178051901272+11,821385913714037i | 123.3718 | 11.8214 | 123.9368 | 5.4733 | 88,31644294524614+0,20423952796804198i | 88.3164 | 0.20424 | 88.3167 | 0.1325 | 35,0553375737659+11,617146385746i | 35.0553 | 11.6171 | 36.9301 | 18.3349 | 62.7068 | 60.2719 | 40.84% | 120.5439 | 6.9343
100 | 5252 | 1572 | 115,3142356406401+12,903692136939181i | 115.3142 | 12.9037 | 116.034 | 6.3849 | 84,37010401936651+0,22694099979149726i | 84.3701 | 0.22694 | 84.3704 | 0.15412 | 30,9441316212735+12,6767511371476i | 30.9441 | 12.6768 | 33.4401 | 22.2772 | 62.7068 | 52.1128 | 34.55% | 104.2255 | 8.0199
150 | 5252 | 1572 | 98,31577405998357+19,42804512622435i | 98.3158 | 19.428 | 100.217 | 11.1781 | 75,05120422185033+0,3426191305390371i | 75.0512 | 0.34262 | 75.052 | 0.26156 | 23,2645698381332+19,0854259956853i | 23.2646 | 19.0854 | 30.0914 | 39.3642 | 62.7068 | 34.5447 | 19.69% | 69.0895 | 12.0985
200 | 5252 | 1572 | 91,18430408833107+26,019384046726238i | 91.1843 | 26.0194 | 94.824 | 15.9261 | 69,2923870469905+0,45949089674793553i | 69.2924 | 0.45949 | 69.2939 | 0.37993 | 21,8919170413405+25,5598931499783i | 21.8919 | 25.5599 | 33.6536 | 49.4201 | 62.7068 | 26.7623 | 10.5% | 53.5246 | 15.6168
250 | 5252 | 1572 | 85,73481836180828+33,20662528432844i | 85.7348 | 33.2066 | 91.941 | 21.1723 | 66,07795449485113+0,5591923998447136i | 66.078 | 0.55919 | 66.0803 | 0.48486 | 19,6568638669571+32,6474328844837i | 19.6569 | 32.6474 | 38.1084 | 58.9481 | 62.7068 | 20.6079 | 5.38% | 41.2157 | 20.2806
300 | 5252 | 1572 | 83,77014639378615+39,32409310881937i | 83.7701 | 39.3241 | 92.5409 | 25.1467 | 64,13785276258086+0,6551275577360918i | 64.1379 | 0.65513 | 64.1412 | 0.58522 | 19,6322936312053+38,6689655510832i | 19.6323 | 38.669 | 43.3672 | 63.083 | 62.7068 | 17.9109 | 2.287% | 35.8219 | 23.3344
350 | 5252 | 1572 | 82,54738208200419+43,11044355270931i | 82.5474 | 43.1104 | 93.1267 | 27.5759 | 62,82509598666638+0,7658600486072374i | 62.8251 | 0.76586 | 62.8298 | 0.69842 | 19,7222860953378+42,3445835041021i | 19.7223 | 42.3446 | 46.7122 | 65.0259 | 62.7068 | 15.9354 | 0.1961% | 31.8708 | 26.2272
400 | 5252 | 1572 | 80,80192406673201+49,08620296541348i | 80.8019 | 49.0862 | 94.5431 | 31.2782 | 61,648984804660195+0,8219745737187678i | 61.649 | 0.82197 | 61.6545 | 0.76389 | 19,1529392620719+48,2642283916946i | 19.1529 | 48.2642 | 51.9256 | 68.3551 | 62.7068 | 13.4211 | -1.678% | 26.8421 | 31.1407
500 | 5252 | 1572 | 79,64679425060376+59,48953266784069i | 79.6468 | 59.4895 | 99.4113 | 36.7567 | 60,1172203087024+1,0340578810431533i | 60.1172 | 1.0341 | 60.1261 | 0.98543 | 19,5295739419013+58,4554747867975i | 19.5296 | 58.4555 | 61.6315 | 71.5259 | 62.7068 | 10.7025 | -4.115% | 21.405 | 39.0508
600 | 5252 | 1572 | 80,14254490469966+71,6832819788123i | 80.1425 | 71.6833 | 107.5236 | 41.811 | 59,12260239665112+1,136761557708654i | 59.1226 | 1.1368 | 59.1335 | 1.1015 | 21,0199425080485+70,5465204211037i | 21.0199 | 70.5465 | 73.6115 | 73.4081 | 62.7068 | 9.6184 | -5.698% | 19.2369 | 43.452
800 | 5252 | 1572 | 80,23169847142009+88,0486311557862i | 80.2317 | 88.0486 | 119.1205 | 47.6596 | 57,87541322760945+1,5208244995279876i | 57.8754 | 1.5208 | 57.8954 | 1.5052 | 22,3562852438106+86,5278066562582i | 22.3563 | 86.5278 | 89.3693 | 75.5132 | 62.7068 | 6.5155 | -7.673% | 13.031 | 64.1457
1000 | 5252 | 1572 | 82,20657231043386+107,32696573052041i | 82.2066 | 107.327 | 135.1924 | 52.5499 | 57,28525674907567+1,7720137981148978i | 57.2853 | 1.772 | 57.3127 | 1.7718 | 24,9213155613582+105,554951932405i | 24.9213 | 105.555 | 108.457 | 76.7158 | 62.7068 | 5.1345 | -8.602% | 10.2689 | 81.3993
1500 | 5252 | 1572 | 88,61779578153828+177,42835497440151i | 88.6178 | 177.4284 | 198.3278 | 63.4599 | 56,953+2,338i | 56.953 | 2.338 | 57.001 | 2.3508 | 31,6647957815382+175,090354974401i | 31.6648 | 175.0904 | 177.9306 | 79.749 | 62.7068 | 4.8292 | -9.099% | 9.6585 | 86.544
10 | 10240 | 0 | 659,3873486978952-6,064229988274033E-8i | 659.3873 | -6.0642e-08 | 659.3873 | -5.2694e-09 | 534,8642051962302-4,643986796780197E-8i | 534.8642 | -4.644e-08 | 534.8642 | -4.9747e-09 | 124,523143501665-1,42024319149384E-08i | 124.5231 | -1.4202e-08 | 124.5231 | -6.5348e-09 | 122.2616 | 537.1258 | 337.5% | 1074.2516 | 1.5171
20 | 10240 | 0 | 480,13773184043754-4,594601960592834E-8i | 480.1377 | -4.5946e-08 | 480.1377 | -5.4828e-09 | 362,2622838257628-3,2239787110497954E-8i | 362.2623 | -3.224e-08 | 362.2623 | -5.0991e-09 | 117,875448014675-1,37062324954304E-08i | 117.8754 | -1.3706e-08 | 117.8754 | -6.6622e-09 | 122.2616 | 357.8762 | 196.3% | 715.7523 | 2.277
30 | 10240 | 0 | 398,6334902092126-3,886950772219933E-8i | 398.6335 | -3.887e-08 | 398.6335 | -5.5867e-09 | 287,29906719226716-2,5896414483959245E-8i | 287.2991 | -2.5896e-08 | 287.2991 | -5.1645e-09 | 111,334423016945-1,29730932382401E-08i | 111.3344 | -1.2973e-08 | 111.3344 | -6.6763e-09 | 122.2616 | 276.3719 | 135% | 552.7439 | 2.9485
40 | 10240 | 0 | 344,560262356481-3,4246860775938035E-8i | 344.5603 | -3.4247e-08 | 344.5603 | -5.6948e-09 | 245,48617171923127-2,2364695545424593E-8i | 245.4862 | -2.2365e-08 | 245.4862 | -5.2199e-09 | 99,07409063725-1,18821652305135E-08i | 99.0741 | -1.1882e-08 | 99.0741 | -6.8716e-09 | 122.2616 | 222.2987 | 100.8% | 444.5974 | 3.6657
50 | 10240 | 0 | 311,5647806647879-3,111326848028765E-8i | 311.5648 | -3.1113e-08 | 311.5648 | -5.7216e-09 | 219,1457773123735-2,0036113226607923E-8i | 219.1458 | -2.0036e-08 | 219.1458 | -5.2385e-09 | 92,419003352414-1,10771552536797E-08i | 92.419 | -1.1077e-08 | 92.419 | -6.8674e-09 | 122.2616 | 189.3032 | 79.24% | 378.6064 | 4.3046
60 | 10240 | 0 | 286,5624309471847-2,8620178702117675E-8i | 286.5624 | -2.862e-08 | 286.5624 | -5.7224e-09 | 201,41994897979276-1,8575480361398462E-8i | 201.4199 | -1.8575e-08 | 201.4199 | -5.284e-09 | 85,142481967392-1,00446983407192E-08i | 85.1425 | -1.0045e-08 | 85.1425 | -6.7595e-09 | 122.2616 | 164.3009 | 64.75% | 328.6017 | 4.9596
70 | 10240 | 0 | 259,7881909777142-5,5188040677660805E-8i | 259.7882 | -5.5188e-08 | 259.7882 | -1.2172e-08 | 189,7185045317029-1,74891809842377E-8i | 189.7185 | -1.7489e-08 | 189.7185 | -5.2818e-09 | 70,069686446012-3,76988596934231E-08i | 70.0697 | -3.7699e-08 | 70.0697 | -3.0826e-08 | 122.2616 | 137.5266 | 55.17% | 275.0533 | 5.9252
80 | 10240 | 0 | 250,66958153875308-2,5152477681750018E-8i | 250.6696 | -2.5152e-08 | 250.6696 | -5.7491e-09 | 178,72888115629263-1,6505811898217138E-8i | 178.7289 | -1.6506e-08 | 178.7289 | -5.2913e-09 | 71,940700382461-8,6466657835329E-09i | 71.9407 | -8.6467e-09 | 71.9407 | -6.8865e-09 | 122.2616 | 128.408 | 46.19% | 256.816 | 6.346
90 | 10240 | 0 | 239,77558145733045-1,3311979200707953E-4i | 239.7756 | -0.00013312 | 239.7756 | -3.181e-05 | 169,6598264237811-1,5683539753805727E-8i | 169.6598 | -1.5684e-08 | 169.6598 | -5.2965e-09 | 70,115755033549-0,000133104108467325i | 70.1158 | -0.0001331 | 70.1158 | -0.00010877 | 122.2616 | 117.514 | 38.77% | 235.028 | 6.9343
100 | 10240 | 0 | 223,86610286100907-2,248502628623356E-8i | 223.8661 | -2.2485e-08 | 223.8661 | -5.7548e-09 | 163,21515296288013-1,5202549491535402E-8i | 163.2152 | -1.5203e-08 | 163.2152 | -5.3368e-09 | 60,650949898129-7,2824767946981E-09i | 60.6509 | -7.2825e-09 | 60.6509 | -6.8796e-09 | 122.2616 | 101.6045 | 33.5% | 203.2091 | 8.02
150 | 10240 | 0 | 189,61465428683678-1,6261248875577913E-8i | 189.6147 | -1.6261e-08 | 189.6147 | -4.9137e-09 | 141,29450483412168-1,3065478149309383E-8i | 141.2945 | -1.3065e-08 | 141.2945 | -5.2981e-09 | 48,320149452715-3,1957707262686E-09i | 48.3201 | -3.1958e-09 | 48.3201 | -3.7894e-09 | 122.2616 | 67.3531 | 15.57% | 134.7062 | 12.0985
200 | 10240 | 0 | 174,44122959740798-1,6587753274024125E-8i | 174.4412 | -1.6588e-08 | 174.4412 | -5.4483e-09 | 134,11555013553823-1,2429191435174085E-8i | 134.1156 | -1.2429e-08 | 134.1156 | -5.3099e-09 | 40,325679461869-4,1585618388501E-09i | 40.3257 | -4.1586e-09 | 40.3257 | -5.9086e-09 | 122.2616 | 52.1797 | 9.696% | 104.3593 | 15.6167
250 | 10240 | 0 | 162,44154004475382+5,857204291898622E-6i | 162.4415 | 5.8572e-06 | 162.4415 | 2.0659e-06 | 127,69415964554214-1,1796259257773292E-8i | 127.6942 | -1.1796e-08 | 127.6942 | -5.2929e-09 | 34,747380399211+5,86900055115639E-06i | 34.7474 | 5.869e-06 | 34.7474 | 9.6775e-06 | 122.2616 | 40.18 | 4.443% | 80.36 | 20.2806
300 | 10240 | 0 | 157,18311400123852-1,652533140828632E-8i | 157.1831 | -1.6525e-08 | 157.1831 | -6.0237e-09 | 124,56941955541586-1,1636507295614903E-8i | 124.5694 | -1.1637e-08 | 124.5694 | -5.3522e-09 | 32,613694445823-4,8888241126714E-09i | 32.6137 | -4.8888e-09 | 32.6137 | -8.5887e-09 | 122.2616 | 34.9216 | 1.888% | 69.8431 | 23.3344
350 | 10240 | 0 | 153,3307006944114-1,1767062364053785E-7i | 153.3307 | -1.1767e-07 | 153.3307 | -4.3971e-08 | 119,41670896759423-3,182094671848063E-8i | 119.4167 | -3.1821e-08 | 119.4167 | -1.5268e-08 | 33,913991726817-8,58496769220564E-08i | 33.914 | -8.585e-08 | 33.914 | -1.4504e-07 | 122.2616 | 31.0691 | -2.327% | 62.1383 | 26.2277
400 | 10240 | 0 | 148,42866780178585+5,405071934868757E-8i | 148.4287 | 5.4051e-08 | 148.4287 | 2.0864e-08 | 117,00495552931575-1,074633601979057E-8i | 117.005 | -1.0746e-08 | 117.005 | -5.2623e-09 | 31,42371227247+6,4797055368478E-08i | 31.4237 | 6.4797e-08 | 31.4237 | 1.1815e-07 | 122.2616 | 26.1671 | -4.299% | 52.3342 | 31.1411
500 | 10240 | 0 | 143,12904739134703-3,5199577587378066E-4i | 143.129 | -0.000352 | 143.129 | -0.00014091 | 114,95804628817473-1,0540308722111298E-8i | 114.958 | -1.054e-08 | 114.958 | -5.2534e-09 | 28,171001103173-0,000351985235565058i | 28.171 | -0.00035199 | 28.171 | -0.00071589 | 122.2616 | 20.8675 | -5.974% | 41.735 | 39.0499
600 | 10240 | 0 | 141,01536419026274+5,356913676374194E-5i | 141.0154 | 5.3569e-05 | 141.0154 | 2.1766e-05 | 115,13864907047146+2,2624532873285614E-8i | 115.1386 | 2.2625e-08 | 115.1386 | 1.1259e-08 | 25,876715119791+0,0000535465122308686i | 25.8767 | 5.3547e-05 | 25.8767 | 0.00011856 | 122.2616 | 18.7538 | -5.826% | 37.5076 | 43.4511
800 | 10240 | 0 | 134,96550873061133-1,2959916920248797E-8i | 134.9655 | -1.296e-08 | 134.9655 | -5.5018e-09 | 111,1717003391747-1,0164841842549899E-8i | 111.1717 | -1.0165e-08 | 111.1717 | -5.2388e-09 | 23,793808391437-2,7950750776989E-09i | 23.7938 | -2.7951e-09 | 23.7938 | -6.7306e-09 | 122.2616 | 12.7039 | -9.071% | 25.4079 | 64.1433
1000 | 10240 | 0 | 132,27230269623107-1,114237810134245E-8i | 132.2723 | -1.1142e-08 | 132.2723 | -4.8265e-09 | 110,937207961716+1,9898357611864976E-6i | 110.9372 | 1.9898e-06 | 110.9372 | 1.0277e-06 | 21,335094734515-2,00097813928783E-06i | 21.3351 | -2.001e-06 | 21.3351 | -5.3737e-06 | 122.2616 | 10.0107 | -9.262% | 20.0215 | 81.3999
1500 | 10240 | 0 | 131,67737287834888-1,3030756450546234E-8i | 131.6774 | -1.3031e-08 | 131.6774 | -5.67e-09 | 109,94224770462365-9,415430761879132E-9i | 109.9422 | -9.4154e-09 | 109.9422 | -4.9068e-09 | 21,735125173725-3,61532568866707E-09i | 21.7351 | -3.6153e-09 | 21.7351 | -9.5303e-09 | 122.2616 | 9.4158 | -10.08% | 18.8316 | 86.5431
10 | 10240 | 1572 | 656,7211842057479+0,11508328752759339i | 656.7212 | 0.11508 | 656.7212 | 0.01004 | 537,6906000422512-0,6507147604225616i | 537.6906 | -0.65071 | 537.691 | -0.069339 | 119,030584163496+0,765798047950154i | 119.0306 | 0.7658 | 119.033 | 0.36861 | 122.2616 | 537.1258 | 339.8% | 1074.2516 | 1.5171
20 | 10240 | 1572 | 479,06817713780333+1,587473450209327i | 479.0682 | 1.5875 | 479.0708 | 0.18986 | 362,866792598403-0,40498969035354276i | 362.8668 | -0.40499 | 362.867 | -0.063947 | 116,2013845394+1,99246314056286i | 116.2014 | 1.9925 | 116.2185 | 0.98233 | 122.2616 | 357.8762 | 196.8% | 715.7523 | 2.277
30 | 10240 | 1572 | 398,02421514817956+3,0185294279488666i | 398.0242 | 3.0185 | 398.0357 | 0.43451 | 288,0966532845554-0,28230982310268044i | 288.0967 | -0.28231 | 288.0968 | -0.056145 | 109,927561863624+3,30083925105154i | 109.9276 | 3.3008 | 109.9771 | 1.7199 | 122.2616 | 276.3719 | 135.6% | 552.7439 | 2.9485
40 | 10240 | 1572 | 344,18476333769576+4,428903942699385i | 344.1848 | 4.4289 | 344.2133 | 0.73723 | 247,143535712618-0,2037278217028058i | 247.1435 | -0.20373 | 247.1436 | -0.047231 | 97,041227625077+4,63263176440219i | 97.0412 | 4.6326 | 97.1517 | 2.7332 | 122.2616 | 222.2987 | 102.1% | 444.5974 | 3.6657
50 | 10240 | 1572 | 311,34462504725803+5,84773150870341i | 311.3446 | 5.8477 | 311.3995 | 1.076 | 220,96969682226478-0,14538293208355066i | 220.9697 | -0.14538 | 220.9697 | -0.037697 | 90,374928224994+5,99311444078696i | 90.3749 | 5.9931 | 90.5734 | 3.794 | 122.2616 | 189.3032 | 80.74% | 378.6064 | 4.3046
60 | 10240 | 1572 | 286,4651964335614+7,32726471690621i | 286.4652 | 7.3273 | 286.5589 | 1.4652 | 203,07998090615118-0,09572848599113608i | 203.08 | -0.095728 | 203.08 | -0.027008 | 83,38521552741+7,42299320289735i | 83.3852 | 7.423 | 83.715 | 5.0871 | 122.2616 | 164.3009 | 66.1% | 328.6017 | 4.9596
70 | 10240 | 1572 | 259,7968858706658+8,761996220297638i | 259.7969 | 8.762 | 259.9446 | 1.9316 | 190,97699625069802-0,05672074501783249i | 190.977 | -0.056721 | 190.977 | -0.017017 | 68,819889619967+8,81871696531546i | 68.8199 | 8.8187 | 69.3826 | 7.3022 | 122.2616 | 137.5266 | 56.2% | 275.0533 | 5.9252
80 | 10240 | 1572 | 250,77546140525507+10,070689685800701i | 250.7755 | 10.0707 | 250.9776 | 2.2997 | 178,99230936177037-0,016641288998456835i | 178.9923 | -0.016641 | 178.9923 | -0.0053269 | 71,783152043485+10,0873309747992i | 71.7832 | 10.0873 | 72.4884 | 7.9991 | 122.2616 | 128.408 | 46.4% | 256.816 | 6.346
90 | 10240 | 1572 | 239,97636503043702+11,708960096793719i | 239.9764 | 11.709 | 240.2618 | 2.7934 | 172,19103715098902+0,015700239962907366i | 172.191 | 0.0157 | 172.191 | 0.0052242 | 67,785327879448+11,6932598568308i | 67.7853 | 11.6933 | 68.7865 | 9.7874 | 122.2616 | 117.514 | 40.84% | 235.028 | 6.9343
100 | 10240 | 1572 | 224,16184247689566+12,83948157818893i | 224.1618 | 12.8395 | 224.5292 | 3.2782 | 164,49633262288322+0,04706169012863828i | 164.4963 | 0.047062 | 164.4963 | 0.016392 | 59,665509854012+12,7924198880603i | 59.6655 | 12.7924 | 61.0215 | 12.1011 | 122.2616 | 101.6045 | 34.54% | 203.2091 | 8.02
150 | 10240 | 1572 | 190,40788078692938+19,607918794582663i | 190.4079 | 19.6079 | 191.4148 | 5.8795 | 146,3242329055168+0,18194890587573573i | 146.3242 | 0.18195 | 146.3243 | 0.071245 | 44,083647881413+19,4259698887069i | 44.0836 | 19.426 | 48.174 | 23.7812 | 122.2616 | 67.3531 | 19.68% | 134.7062 | 12.0985
200 | 10240 | 1572 | 175,80483666903731+26,478714324532504i | 175.8048 | 26.4787 | 177.7877 | 8.5652 | 135,09167637257934+0,31129910285240964i | 135.0917 | 0.3113 | 135.092 | 0.13203 | 40,713160296458+26,1674152216801i | 40.7132 | 26.1674 | 48.3973 | 32.7299 | 122.2616 | 52.1797 | 10.49% | 104.3593 | 15.6167
250 | 10240 | 1572 | 164,4403505935494+33,978187453680896i | 164.4404 | 33.9782 | 167.9141 | 11.6747 | 128,8189907858731+0,4189672271250718i | 128.819 | 0.41897 | 128.8197 | 0.18635 | 35,621359807676+33,5592202265557i | 35.6214 | 33.5592 | 48.9398 | 43.2926 | 122.2616 | 40.18 | 5.364% | 80.36 | 20.2806
300 | 10240 | 1572 | 159,85970328944214+40,418148202688485i | 159.8597 | 40.4181 | 164.8901 | 14.189 | 125,0293880184957+0,5200453065891519i | 125.0294 | 0.52005 | 125.0305 | 0.23831 | 34,830315270947+39,8981028960992i | 34.8303 | 39.8981 | 52.9623 | 48.8796 | 122.2616 | 34.9216 | 2.265% | 69.8431 | 23.3344
350 | 10240 | 1572 | 156,71811733782536+44,53611468996274i | 156.7181 | 44.5361 | 162.9234 | 15.8641 | 122,46018705877454+0,6348864513813377i | 122.4602 | 0.63489 | 122.4618 | 0.29704 | 34,257930279051+43,9012282385814i | 34.2579 | 43.9012 | 55.6859 | 52.0336 | 122.2616 | 31.0691 | 0.1638% | 62.1383 | 26.2277
400 | 10240 | 1572 | 152,55008699799959+50,850359375927674i | 152.5501 | 50.8504 | 160.802 | 18.4351 | 120,15954875023336+0,6945449383441276i | 120.1595 | 0.69454 | 120.1616 | 0.33118 | 32,390538247766+50,1558144375835i | 32.3905 | 50.1558 | 59.7055 | 57.1457 | 122.2616 | 26.1671 | -1.718% | 52.3342 | 31.1411
500 | 10240 | 1572 | 148,7582464634923+61,929840828180694i | 148.7582 | 61.9298 | 161.1345 | 22.6025 | 117,14273424004118+0,9137618561615657i | 117.1427 | 0.91376 | 117.1463 | 0.44692 | 31,615512223451+61,016078972019i | 31.6155 | 61.0161 | 68.7205 | 62.609 | 122.2616 | 20.8675 | -4.184% | 41.735 | 39.0499
600 | 10240 | 1572 | 148,1839968808163+74,79816923343041i | 148.184 | 74.7982 | 165.9918 | 26.7831 | 115,18047459387522+1,0223991418776996i | 115.1805 | 1.0224 | 115.185 | 0.50857 | 33,003522286941+73,7757700915527i | 33.0035 | 73.7758 | 80.8214 | 65.8987 | 122.2616 | 18.7538 | -5.788% | 37.5076 | 43.4511
800 | 10240 | 1572 | 145,26418097280185+92,5246387214472i | 145.2642 | 92.5246 | 172.228 | 32.4947 | 112,63757060284654+1,4265318390736126i | 112.6376 | 1.4265 | 112.6466 | 0.7256 | 32,626610369955+91,0981068823736i | 32.6266 | 91.0981 | 96.7645 | 70.2951 | 122.2616 | 12.7039 | -7.864% | 25.4079 | 64.1433
1000 | 10240 | 1572 | 145,82405908147382+113,21008704597985i | 145.8241 | 113.2101 | 184.6109 | 37.8239 | 111,38161630927372+1,7006676665543068i | 111.3816 | 1.7007 | 111.3946 | 0.87477 | 34,4424427722+111,509419379425i | 34.4424 | 111.5094 | 116.7075 | 72.8354 | 122.2616 | 10.0107 | -8.888% | 20.0215 | 81.3999
1500 | 10240 | 1572 | 150,36144872302634+186,87912175970516i | 150.3614 | 186.8791 | 239.8591 | 51.1801 | 110,31+2,3831i | 110.31 | 2.3831 | 110.3357 | 1.2376 | 40,051448723026+184,496021759705i | 40.0514 | 184.496 | 188.7933 | 77.7519 | 122.2616 | 9.4158 | -9.754% | 18.8316 | 86.5431