## Section 3 Results
Results obtained by computer simulation of the case study using COMSOL ( Electromagnetic Field Modeling ) and ATP ( Lumped Parameter Modeling )
INPUT PARAMETERS | [14 empty] | COMPUTACIONAL SIMULATION RESULTS
Project data | [7 empty] | Lumped parameter modeling according Section 3 | [6 empty] | Electromagnetic Field Modeling using COMSOL |  |  |  |  | Lumped parameter modeling using ATP
L (m) | h (m) | p (Ω.m) | Cg (m) | pcu(Ω/mm².km) | A (mm²) | Rs (Ω/km) | Zs (Ω/km) | Zs_lumped (Ω) | Rp_lumped (Ω) | Rs_lumped (Ω) | Lp_lumped (H) | Rf (Ω) | k | Rc (Ω) | Lumped port impedance (Ω) | R (Ω) | X (Ω) | ¦Zmed¦ (Ω) | θ (°) | ¦Zmed¦(Ω) [23] | PE_LPM (%) [23] | ¦Zmed¦(Ω) [Proposed] | PE_LPM (%) [Proposed]
300 | 1 | 100 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,75613335208976i | 0,0690868268663922+0,226840005626928i | 0.88093 | 0.069087 | 2.2966e-05 | 1.2168 | 0.7 | 4.8947 | 1,3439069021425247+0,5298764706375344i | 1.3439 | 0.52988 | 1.4446 | 21.5184 | 1.7433 | 20.68% | 1.2893 | -10.75%
300 | 1 | 300 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,790629777953939i | 0,0690868268663922+0,237188933386182i | 2.6428 | 0.069087 | 2.4014e-05 | 3.6504 | 0.7 | 14.6841 | 3,582376770583496+0,7067946590924175i | 3.5824 | 0.70679 | 3.6514 | 11.161 | 4.7934 | 31.27% | 3.4972 | -4.224%
300 | 1 | 5252 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,880514845242007i | 0,0690868268663922+0,264154453572602i | 46.2663 | 0.069087 | 2.6744e-05 | 63.907 | 0.7 | 257.071 | 59,91921539522289+0,7443470526300021i | 59.9192 | 0.74435 | 59.9238 | 0.71172 | 80.5331 | 34.39% | 59.456 | -0.7807%
300 | 1 | 10240 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,90148039486557i | 0,0690868268663922+0,270444118459671i | 90.2069 | 0.069087 | 2.7381e-05 | 124.6 | 0.7 | 501.2162 | 116,79795067665087+0,6319137801647258i | 116.798 | 0.63191 | 116.7997 | 0.30999 | 154.3222 | 32.13% | 115.91 | -0.7617%
300 | 1 | 2100 | 0.0055 | 17.2 | 95.0332 | 0.18099 | 0,230289422887974+0,851731356634276i | 0,0690868268663922+0,255519406990283i | 18.4995 | 0.069087 | 2.587e-05 | 4.1899 | 0.7 | 52.9419 | 6,04335854491927+2,965067414146472i | 6.0434 | 2.9651 | 6.7316 | 26.1341 | 8.8542 | 31.53% | 5.989 | -11.03%
Where:
L is the length of the horizontal electrode (m)
h is the depth of burial (m)
ρ is the medium earth resistivity (Ω.m)
Cg is the geometric mean radius of the electrode (m)
pcu is the resistivity of copper (Ω/mm².km)
A is the cross-sectional area of the horizontal eletrode (mm2)
Zs is the horizontal electrodes self-impedance (Ω)
Rp is the horizontal electrodes grounding resistance (Ω)
Rf corresponds to the turbine grounding resistance (Ω)
Rs is the series resistance of the horizontal electrode (Ω/km)
Rc is the resistance parallel to the measurement loop to represent the mutual resistance between the turbine grounding under test and its adjacent horizontal electrode
k is the adjustment parameter introduced to tuning the model
PE_LPM is the percentage error of the lumped parameter modeling (%)

## Section 4 Results
Parameter k survey for the case study.
Results obtained by computer simulation of the case study in COMSOL Multiphisics
L (m) | ρ (m) | Rmed_wire_10L (Ω) | Rmed_wire_11.4m (Ω) | Rf (Ω) | Rp (Ω) | 2.Rp (Ω) | Semi-sphere_rp(Ω) | Rmed_lumped_11.4m (Ω) | AE | k
80 | 20 | 0.48959 | 0.34908 | 0.23879 | 0.2508 | 0.50159 | 6.346 | 0.36426 | -0.25599 | 0.74401
90 | 20 | 0.46831 | 0.33137 | 0.23879 | 0.22952 | 0.45904 | 6.9343 | 0.34517 | -0.26295 | 0.73705
100 | 20 | 0.43724 | 0.31878 | 0.23879 | 0.19845 | 0.3969 | 8.02 | 0.31764 | -0.27353 | 0.72647
150 | 20 | 0.37034 | 0.27596 | 0.23879 | 0.13155 | 0.2631 | 12.0986 | 0.26057 | -0.2964 | 0.7036
200 | 20 | 0.3407 | 0.26195 | 0.23879 | 0.10191 | 0.20382 | 15.6169 | 0.23683 | -0.30488 | 0.69512
250 | 20 | 0.31727 | 0.2494 | 0.23879 | 0.078476 | 0.15695 | 20.2806 | 0.21916 | -0.30923 | 0.69077
300 | 20 | 0.307 | 0.2433 | 0.23879 | 0.068206 | 0.13641 | 23.3345 | 0.21183 | -0.31 | 0.69
350 | 20 | 0.29948 | 0.23324 | 0.23879 | 0.060683 | 0.12137 | 26.2272 | 0.20666 | -0.30993 | 0.69007
400 | 20 | 0.2899 | 0.22853 | 0.23879 | 0.051108 | 0.10222 | 31.1408 | 0.20029 | -0.30911 | 0.69089
500 | 20 | 0.27955 | 0.22453 | 0.23879 | 0.040756 | 0.081512 | 39.0506 | 0.19377 | -0.30685 | 0.69315
600 | 20 | 0.27542 | 0.22488 | 0.23879 | 0.036629 | 0.073258 | 43.4508 | 0.19131 | -0.30539 | 0.69461
800 | 20 | 0.2636 | 0.21713 | 0.23879 | 0.024812 | 0.049625 | 64.1434 | 0.18605 | -0.29421 | 0.70579
80 | 100 | 2.4479 | 1.7454 | 1.194 | 1.254 | 2.508 | 6.346 | 1.8213 | -0.25599 | 0.74401
90 | 100 | 2.3416 | 1.6568 | 1.194 | 1.1476 | 2.2952 | 6.9343 | 1.7258 | -0.26297 | 0.73703
100 | 100 | 2.1862 | 1.5939 | 1.194 | 0.99224 | 1.9845 | 8.02 | 1.5882 | -0.27353 | 0.72647
150 | 100 | 1.8517 | 1.3798 | 1.194 | 0.65774 | 1.3155 | 12.0986 | 1.3029 | -0.29638 | 0.70362
200 | 100 | 1.7035 | 1.3097 | 1.194 | 0.50956 | 1.0191 | 15.6169 | 1.1842 | -0.30485 | 0.69515
250 | 100 | 1.5863 | 1.247 | 1.194 | 0.39238 | 0.78476 | 20.2807 | 1.0958 | -0.30923 | 0.69077
300 | 100 | 1.535 | 1.2165 | 1.194 | 0.34103 | 0.68206 | 23.3344 | 1.0592 | -0.30996 | 0.69004
350 | 100 | 1.4974 | 1.1662 | 1.194 | 0.30341 | 0.60682 | 26.2277 | 1.0333 | -0.30992 | 0.69008
400 | 100 | 1.4495 | 1.1426 | 1.194 | 0.25554 | 0.51108 | 31.141 | 1.0015 | -0.30907 | 0.69093
500 | 100 | 1.3977 | 1.1226 | 1.194 | 0.20378 | 0.40756 | 39.0508 | 0.96883 | -0.30686 | 0.69314
600 | 100 | 1.3771 | 1.1244 | 1.194 | 0.18314 | 0.36628 | 43.452 | 0.95656 | -0.30538 | 0.69462
800 | 100 | 1.318 | 1.0857 | 1.194 | 0.12406 | 0.24813 | 64.1428 | 0.93024 | -0.29422 | 0.70578
80 | 300 | 7.3438 | 5.2362 | 3.5819 | 3.7619 | 7.5239 | 6.346 | 5.4639 | -0.25599 | 0.74401
90 | 300 | 7.0247 | 4.9705 | 3.5819 | 3.4428 | 6.8856 | 6.9343 | 5.1775 | -0.26295 | 0.73705
100 | 300 | 6.5586 | 4.7817 | 3.5819 | 2.9767 | 5.9534 | 8.02 | 4.7647 | -0.27352 | 0.72648
150 | 300 | 5.5551 | 4.1395 | 3.5819 | 1.9732 | 3.9465 | 12.0985 | 3.9086 | -0.2964 | 0.7036
200 | 300 | 5.1106 | 3.9292 | 3.5819 | 1.5287 | 3.0574 | 15.6169 | 3.5525 | -0.30487 | 0.69513
250 | 300 | 4.759 | 3.741 | 3.5819 | 1.1771 | 2.3543 | 20.2805 | 3.2875 | -0.30921 | 0.69079
300 | 300 | 4.6049 | 3.6495 | 3.5819 | 1.0231 | 2.0461 | 23.3351 | 3.1775 | -0.30998 | 0.69002
350 | 300 | 4.4921 | 3.4985 | 3.5819 | 0.91024 | 1.8205 | 26.2275 | 3.1 | -0.3099 | 0.6901
400 | 300 | 4.3485 | 3.4279 | 3.5819 | 0.76662 | 1.5332 | 31.141 | 3.0044 | -0.3091 | 0.6909
500 | 300 | 4.1932 | 3.3679 | 3.5819 | 0.61134 | 1.2227 | 39.0509 | 2.9065 | -0.30686 | 0.69314
600 | 300 | 4.1313 | 3.3732 | 3.5819 | 0.54942 | 1.0988 | 43.4516 | 2.8697 | -0.30538 | 0.69462
800 | 300 | 3.9541 | 3.257 | 3.5819 | 0.37218 | 0.74436 | 64.1439 | 2.7907 | -0.29422 | 0.70578
80 | 5252 | 128.5664 | 91.6683 | 62.7068 | 65.8596 | 131.7193 | 6.3459 | 95.656 | -0.25598 | 0.74402
90 | 5252 | 122.9787 | 87.0173 | 62.7068 | 60.2719 | 120.5439 | 6.9343 | 90.641 | -0.26295 | 0.73705
100 | 5252 | 114.8196 | 83.7113 | 62.7068 | 52.1128 | 104.2255 | 8.0199 | 83.413 | -0.27353 | 0.72647
150 | 5252 | 97.2516 | 72.4684 | 62.7068 | 34.5447 | 69.0895 | 12.0985 | 68.426 | -0.2964 | 0.7036
200 | 5252 | 89.4691 | 68.7868 | 62.7068 | 26.7623 | 53.5246 | 15.6168 | 62.192 | -0.30488 | 0.69512
250 | 5252 | 83.3147 | 65.4931 | 62.7068 | 20.6079 | 41.2157 | 20.2806 | 57.553 | -0.30921 | 0.69079
300 | 5252 | 80.6177 | 63.8902 | 62.7068 | 17.9109 | 35.8219 | 23.3344 | 55.627 | -0.30999 | 0.69001
350 | 5252 | 78.6422 | 61.2476 | 62.7068 | 15.9354 | 31.8708 | 26.2272 | 54.27 | -0.30991 | 0.69009
400 | 5252 | 76.1279 | 60.0108 | 62.7068 | 13.4211 | 26.8421 | 31.1407 | 52.596 | -0.30911 | 0.69089
500 | 5252 | 73.4093 | 58.9608 | 62.7068 | 10.7025 | 21.405 | 39.0508 | 50.883 | -0.30686 | 0.69314
600 | 5252 | 72.3253 | 59.0534 | 62.7068 | 9.6184 | 19.2369 | 43.452 | 50.239 | -0.30537 | 0.69463
800 | 5252 | 69.2223 | 57.0188 | 62.7068 | 6.5155 | 13.031 | 64.1457 | 48.856 | -0.29422 | 0.70578
80 | 10240 | 250.6696 | 178.7289 | 122.2616 | 128.408 | 256.816 | 6.346 | 186.5 | -0.25599 | 0.74401
90 | 10240 | 239.7756 | 169.6598 | 122.2616 | 117.514 | 235.028 | 6.9343 | 176.73 | -0.26294 | 0.73706
100 | 10240 | 223.8661 | 163.2152 | 122.2616 | 101.6045 | 203.2091 | 8.02 | 162.63 | -0.27354 | 0.72646
150 | 10240 | 189.6147 | 141.2945 | 122.2616 | 67.3531 | 134.7062 | 12.0985 | 133.41 | -0.29642 | 0.70358
200 | 10240 | 174.4412 | 134.1156 | 122.2616 | 52.1797 | 104.3593 | 15.6167 | 121.26 | -0.30487 | 0.69513
250 | 10240 | 162.4415 | 127.6942 | 122.2616 | 40.18 | 80.36 | 20.2806 | 112.21 | -0.30923 | 0.69077
300 | 10240 | 157.1831 | 124.5694 | 122.2616 | 34.9216 | 69.8431 | 23.3344 | 108.46 | -0.30998 | 0.69002
350 | 10240 | 153.3307 | 119.4167 | 122.2616 | 31.0691 | 62.1383 | 26.2277 | 105.81 | -0.30992 | 0.69008
400 | 10240 | 148.4287 | 117.005 | 122.2616 | 26.1671 | 52.3342 | 31.1411 | 102.55 | -0.3091 | 0.6909
500 | 10240 | 143.129 | 114.958 | 122.2616 | 20.8675 | 41.735 | 39.0499 | 99.209 | -0.30686 | 0.69314
600 | 10240 | 141.0154 | 115.1386 | 122.2616 | 18.7538 | 37.5076 | 43.4511 | 97.952 | -0.30538 | 0.69462
800 | 10240 | 134.9655 | 111.1717 | 122.2616 | 12.7039 | 25.4079 | 64.1433 | 95.257 | -0.29421 | 0.70579
0.70513
Where:
L is the length of the horizontal electrode (m).
ρ is the medium earth resistivity (Ω.m).
Rmed_wire_10L is the clamp-on reading taken with a distance of 10L between the turbine grounding and the horizontal electrode wire (Ω).
Rmed_wire_11.4m is the clamp-on reading taken with a distance of 11.4 m between the turbine grounding and the horizontal electrode wire (Ω).
Rf is the grounding resistance of the turbine grounding (Ω).
Rp is the grounding resistance of the horizontal electrode (Ω).
Semisphere_rp is the radius of the two semi-spherical electrodes that represent a horizontal electrode according to the lumped parameter modeling (m) .
Rmed_lumped_10L is the clamp-on reading taken with a distance of 10L between the turbine grounding and the horizontal electrode represented by semi-spheres (Ω) .
Rmed_lumped_11.4m is the clamp-on reading taken with a distance of 11.4 m between the turbine grounding and the horizontal electrode represented by semi-spheres (Ω) .
AE is the expected absolute error caused by mutual coupling between nearby electrodes and modeling of the horizontal electrode through lumped parameter (%) => AE = (Rmed_lumped_11.4m - Rmed_wire_10L) / Rmed_wire_10L
k is the adjustment parameter introduced to tuning the model => k = (1 − AE)